## Summary
This workbook contains detailed data that were reviewed as part of the CPUC disposition for the workpaper PGECOHVC174: Multiple Speed Unitary Air-Cooled Commercial Air Conditioners and Heat Pumps >= 65 kBtu/h.
Tab Name | Contents
AllCoefs | Table of input parameters taken from the Manufac.xls workbook. Selected DEER values are added for comparison, and several comments are added. Sample calculations for electric input ratio are provided.
CLOSS | Cycling loss curves used for the workpaper modeling are shown. These are identical to the CLOSS curves used in DEER for the corresponding equipment size category.
EIR_fPLR | Curves for electric input ratio as a function of part load ratio are shown. Workpaper curves are shown along with DEER curves.
ODFan_fPLR | Curves for outdoor fan power as a function of part load ratio are shown. Workpaper curves are shown along with DEER curves.
IDFan_fPLR | Curves for indoor fan power as a function of part load ratio are shown. Workpaper curves are shown along with DEER curves.
Cap_T | Curves for unit total cooling capacity as a function of indoor wet bulb and outdoor dry bulb temperatures are shown. Workpaper curves are shown along with DEER curves.
SCap_T | Curves for unit sensible cooling capacity as a function of indoor wet bulb and outdoor dry bulb temperatures are shown. Workpaper curves are shown along with DEER curves.
EIR_fT | Curves for unit electric input ratio as a function of indoor wet bulb and outdoor dry bulb temperatures are shown. Workpaper curves are shown along with DEER curves.
Savings_65to109 | Energy savings by end use for 65 to 109 kBtu/hr units for vintage 1985 small office building in climate zone 4. Includes comments regarding input parameters that are important to the savings.
Savings_110to239 | Energy savings by end use for 110 to 239 kBtu/hr units for vintage 1985 small office building in climate zone 4. Includes comments regarding input parameters that are important to the savings.
Savings_240to759 | Energy savings by end use for 240 to 759 kBtu/hr units for vintage 1985 small office building in climate zone 4. Includes comments regarding input parameters that are important to the savings.

## AllCoefs
Size Category | Comments | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
Source |  | Workpaper values |  |  |  | DEER values | Workpaper values |  |  | DEER values | Workpaper values |  |  |  | DEER values
Tier Level |  | Code | Tier 1 | Tier 2 | Tier 3 | for reference | Code | Tier 1 | Tier 3 | for reference | Code | Tier 1 | Tier 2 | Tier 3 | for reference
cfm/ton | cfm/ton was not provided; this value is a guess | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 |  | 350 | 350 | 350 | 350
SupFanEIR | dimensionless fan power/unit gross capacity | 0.046687 | 0.027574 | 0.034841 | 0.028171 |  | 0.052378 | 0.040103 | 0.016212 |  | 0.055814 | 0.062204 | 0.0332 | 0.075754
CondFanEIR | dimensionless fan power/unit gross capacity | 0.024622 | 0.026632 | 0.029684 | 0.021395 |  | 0.025112 | 0.022161 | 0.015598 |  | 0.027485 | 0.04252 | 0.034415 | 0.014102
SupFanEIR AHRI | Supply fan power from AHRI test (this value is a guess); AHRI specifies minimum external static in test, this does not reveal actual as-installed fan power | 0.03 | 0.03 | 0.03 | 0.03 |  | 0.02 | 0.02 | 0.02 |  | 0.025 | 0.025 | 0.025 | 0.025
CalcEIR alt | Calc from fixed SupFanEIR AHRI; better would be to have cmp pwr during AHRI test | 0.24634 | 0.21473 | 0.2162 | 0.20725 |  | 0.26459 | 0.232 | 0.24313 |  | 0.28707 | 0.26525 | 0.26366 | 0.28714
MsrEIR/CodeEIR | From calc above |  | 87.17% | 87.76% | 84.13% |  |  | 87.68% | 91.89% |  |  | 92.4% | 91.84% | 100%
MsrEIR/CodeEIR | As modeled |  | 94.71% | 83.86% | 87.81% |  |  | 97.5% | 95.75% |  |  | 87.31% | 90.16% | 90.91%
Manufacturer |  | ManufactuerA | ManufactuerA | ManufacturerA | ManufacturerA |  | ManufactuerA | ManufactuerA | ManufacturerA |  | ManufactuerA | ManufactuerA | ManufactuerA | ManufactuerA
EER (WP msr) |  |  | 12 | 12 | 12 |  |  | 12 | 12 |  |  | 10.2 | 10.2 | 10.2
IEER (WP msr) |  |  | 14 | 16 | 18 | 12.7, 13, 13.5, 15.0 |  | 14 | 17.5 | 12.2, 13, 13.5, 14 |  | 12.3 | 13 | 14.1 | 11.4, 12.2, 12.7, 15.5
EER (modeled) |  | 11 | 12.2 | 12 | 12.8 | 11.0, 11.5, 12.0, 13.0 | 10.8 | 12.2 | 12 | 10.8, 11.5, 12.0, 12.5 | 9.8 | 10 | 10.3 | 10.2 | 9.8, 10.8, 11.5, 12.5
IEER (modeled) | Code IEER = 12.7 for 65 to134 kBtuh | 12.2 | 14 | 16 | 19 | 14.1, 14.3 ,14.6 ,15.1 | 12.2 | 14 | 18 | 13.3, 14.2, 14.8, 15.5 | 11.4 | 12.3 | 13.1 | 14.1 | 11.7, 12.8, 13.6, 14.8
EIR | How calculated? Not consistent with calcs shown above. | 0.24111 | 0.22835 | 0.2022 | 0.21173 | 0.273,0.26,0.247,0.226 | 0.23985 | 0.23386 | 0.22965 | 0.274,0.255,0.243,0.231 | 0.28095 | 0.24531 | 0.2533 | 0.25541 | 0.286,0.255,0.236,0.213
CoilBF | Some significant outliers: are these correct? | 0.09156 | 0.04703 | 0.11237 | 0.011841 | 0.114 | 0.21596 | 0.09048 | 0.0579 | 0.099 | 0.10353 | 0.05292 | 0.14429 | 0.12099 | 0.123
OutFanElec | W/Btuh; is this based on gross or net capacity? | 0.007214 | 0.0078032 | 0.0086973 | 0.0062686 | 0 | 0.0073577 | 0.006493 | 0.0045702 | 0 | 0.0080531 | 0.012458 | 0.010083 | 0.0041317 | 0
InFanElec | kW/cfm; what is the cfm/ ton? Why does it vary so much? | 0.000469 | 0.000277 | 0.00035 | 0.000283 | 0.0004 | 0.00052617 | 0.00040286 | 0.00016286 | 0.00041 | 0.00056069 | 0.00062488 | 0.00033352 | 0.00076099 | 0.61
|  |  | 59.06% | 74.63% | 60.34% |  |  | 76.56% | 30.95% |  |  | 111.4% | 59.48% | 135.7%
MinFlowRatio |  | 0.67 | 0.66 | 0.67 | 0.67 |  | 0.67 | 0.66 | 0.43 |  | 0.66 | 0.66 | 0.66 | 0.6
MinFanRatio |  | 0.67 | 0.66 | 0.67 | 0.67 |  | 0.67 | 0.66 | 0.43 |  | 0.66 | 0.66 | 0.66 | 0.6
MinUnload |  | 0.5 | 0.66 | 0.5 | 0.4 |  | 0.5 | 0.5 | 0.4 |  | 0.498 | 0.271 | 0.285 | 0.507
MinHotGasBPR |  | 0.66 | 0.66 | 0.66 | 0.66 |  | 0.66 | 0.66 | 0.66 |  | 0.66 | 0.66 | 0.66 | 0.66
CoolCaptMin |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
CoolCaptMax |  | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 |  | 2 | 2 | 2 | 2
CoolCaptA |  | 1.8278 | 2.0979 | 1.9466 | 2.4512 |  | 0.7961 | 1.5673 | 2.1393 |  | 0.35974 | 1.2442 | 1.1829 | 1.9899
CoolCaptB |  | -0.035147 | -0.046283 | -0.041065 | -0.053892 |  | -0.010349 | -0.032584 | -0.047194 |  | 0.0043726 | -0.023337 | -0.018985 | -0.042738
CoolCaptC |  | 0.0003706 | 0.00052815 | 0.00048837 | 0.00062116 |  | 0.00012705 | 0.00042738 | 0.00052649 |  | 0.0001145 | 0.00036142 | 0.00027841 | 0.00050981
CoolCaptD |  | 0.0031356 | 0.0050354 | 0.0045741 | 0.0038225 |  | 0.0064175 | 0.0053511 | 0.0039791 |  | 0.0036848 | 0.003208 | 0.0024589 | 0.0036468
CoolCaptE |  | -3.3739e-05 | -1.3858e-05 | -1.3448e-05 | -1.3765e-05 |  | -6.923e-05 | -1.5432e-05 | -1.7252e-05 |  | -1.7347e-05 | -1.6563e-05 | -2.1546e-05 | -1.4924e-05
CoolCaptF |  | -2.0486e-05 | -0.0001135 | -0.00011051 | -0.00013631 |  | 5.3187e-05 | -0.00010622 | -8.8573e-05 |  | -5.7195e-05 | -7.3082e-05 | -3.2504e-05 | -9.9018e-05
SensCaptMin |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
SensCaptMax |  | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 |  | 2 | 2 | 2 | 2
SensCaptA |  | -0.9973 | -1.0537 | -0.94785 | -0.82778 |  | 0.084064 | -0.37935 | 0.030265 |  | 0.66994 | 0.69817 | -0.14712 | 0.60638
SensCaptB |  | 0.10518 | 0.10761 | 0.10575 | 0.11203 |  | 0.065778 | 0.088441 | 0.077635 |  | 0.053415 | 0.060928 | 0.086437 | 0.063787
SensCaptC |  | -0.0011142 | -0.001099 | -0.0010847 | -0.0011462 |  | -0.00084142 | -0.0009627 | -0.00087896 |  | -0.00071998 | -0.0007509 | -0.0010032 | -0.00077242
SensCaptD |  | -0.0072972 | -0.007927 | -0.0081288 | -0.011259 |  | -4.1443e-05 | -0.0071021 | -0.0080329 |  | -0.0031537 | -0.0091246 | -0.0095767 | -0.0088485
SensCaptE |  | -3.1221e-05 | -1.4129e-05 | -1.2814e-05 | -1.5819e-05 |  | -5.9918e-05 | -1.0999e-05 | -1.301e-05 |  | -2.3319e-05 | 4.7908e-06 | -1.3435e-05 | -1.0442e-05
SensCaptF |  | 0.00014644 | 0.00010404 | 9.8444e-05 | 0.00010784 |  | 0.00013373 | 8.8251e-05 | 9.5419e-05 |  | 7.9075e-05 | 6.4977e-05 | 0.00014171 | 8.4366e-05
EIRtMin |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
EIRtMax |  | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 |  | 2 | 2 | 2 | 2
EIRtA |  | -0.32381 | -0.84828 | -0.73966 | -1.1746 |  | 0.18282 | -0.38099 | -0.74524 |  | 0.66919 | -1.1254 | -0.94315 | -0.62239
EIRtB |  | 0.029066 | 0.046132 | 0.040001 | 0.056412 |  | 0.01259 | 0.027315 | 0.039401 |  | -0.0047134 | 0.055333 | 0.043256 | 0.036357
EIRtC |  | -0.00016029 | -0.0003178 | -0.00026233 | -0.00034956 |  | -2.8413e-05 | -0.00017013 | -0.00025912 |  | 0.00018809 | -0.000209 | -0.00010412 | -0.00021723
EIRtD |  | -0.0027393 | -0.0024342 | -0.00096626 | -0.0042889 |  | 0.0026234 | 0.0016291 | 0.0009393 |  | 0.0030347 | -0.00025661 | 0.0042137 | 0.00042774
EIRtE |  | 0.00017205 | 0.0001599 | 0.00015756 | 0.00022087 |  | 0.00013549 | 0.00012739 | 0.00013823 |  | 0.00017723 | 0.000265 | 0.00023326 | 0.00015733
EIRtF |  | -0.00018637 | -0.00016061 | -0.00017054 | -0.00025355 |  | -0.00021339 | -0.00015465 | -0.00016693 |  | -0.00032722 | -0.00047112 | -0.00046851 | -0.00020276
CoilBFtMin |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
CoilBFtMax |  | 6 | 5 | 1.75 | 5 |  | 1.5 | 2 | 2.5 |  | 2 | 2 | 2 | 2
CoilBFtA |  | 77.2555 | 39.0478 | 3.8954 | 44.4881 |  | 3.3655 | 4.5163 | 4.6723 |  | 45.3269 | 111.0618 | 41.9911 | 3.7211
CoilBFtB |  | -2.141 | -1.0171 | -0.042399 | -1.1556 |  | -0.035975 | -0.053228 | -0.054824 |  | -1.3552 | -3.3377 | -1.2187 | -0.041566
CoilBFtC |  | 0.014952 | 0.0067368 | 0 | 0.0075704 |  | 0 | 0 | 0 |  | 0.010295 | 0.025182 | 0.0090129 | 0
CoilBFtD |  | 0 | 0 | 0 | -0.006652 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
CoilBFtE |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
CoilBFtF |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
EIRplrMin |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
EIRplrMax |  | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | 1 | 1
EIRplrA |  | 0 | 0 | 0 | 0.002805 |  | 0 | 0 | 0.0080596 |  | -2.6645e-15 | 0.010907 | -0.0052583 | -0.0018928
EIRplrB |  | 1 | 1 | 1 | 0.75061 |  | 1 | 1 | 0.83829 |  | 0.956 | 0.5652 | 0.68193 | 0.59049
EIRplrC |  | 0 | 0 | 0 | 0.24321 |  | 0 | 0 | 0.14651 |  | 0.044001 | 0.42434 | 0.33272 | 0.41545
EIRplrD |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
CLossplrMin |  | 0.83 | 0.83 | 0.83 | 0.83 |  | 0.8 | 0.8 | 0.8 |  | 0.96 | 0.96 | 0.96 | 0.96
CLossplrMax |  | 1.11 | 1.11 | 1.11 | 1.11 |  | 1.07 | 1.07 | 1.07 |  | 1.3 | 1.3 | 1.3 | 1.3
CLossplrA |  | 0.88228 | 0.88228 | 0.88228 | 0.88228 |  | 0.85236 | 0.85236 | 0.85236 |  | 0.96409 | 0.96409 | 0.96409 | 0.96409
CLossplrB |  | 0.21053 | 0.21053 | 0.21053 | 0.21053 |  | 0.20333 | 0.20333 | 0.20333 |  | 0.28948 | 0.28948 | 0.28948 | 0.28948
CLossplrC |  | -0.04389 | -0.04389 | -0.04389 | -0.04389 |  | -0.04226 | -0.04226 | -0.04226 |  | 0.18252 | 0.18252 | 0.18252 | 0.18252
CLossplrD |  | 0.0098 | 0.0098 | 0.0098 | 0.0098 |  | 0.00938 | 0.00938 | 0.00938 |  | -0.13119 | -0.13119 | -0.13119 | -0.13119
OFanplrMin |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
OFanplrMax |  | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | 1 | 1
OFanplrA |  | 0 | 0 | 0 | -0.002913 |  | 0 | 0 | 0.00073097 |  | 0 | 0 | 0 | -0.00015574
OFanplrB |  | 2 | 1.5152 | 2 | 0.5953 |  | 2 | 2 | 0.67243 |  | 2 | 3.69 | 3.5088 | 0.34955
OFanplrC |  | 0 | 0 | 0 | 0.41127 |  | 0 | 0 | 0.32607 |  | 0 | 0 | 0 | 0.65091
OFanplrD |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
FanEIRplrMin |  | 0.3 | 0.29 | 0.3 | 0.3 |  | 0.29 | 0.29 | 0.08 |  | 0.28 | 0.22 | 0.28 | 0.22
FanEIRplrMax |  | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | 1 | 1
FanEIRplrA |  | -1.1189 | -1.0956 | -1.1189 | -1.1189 |  | -1.0956 | -1.0956 | 0.2451 |  | -1.0956 | -1.0956 | -1.0956 | 0.432
FanEIRplrB |  | 2.1189 | 2.0956 | 2.1189 | 2.1189 |  | 2.0956 | 2.0956 | -1.2451 |  | 2.0956 | 2.0956 | 2.0956 | -1.752
FanEIRplrC |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 2 |  | 0 | 0 | 0 | 2.32
FanEIRplrD |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Note on H14: This is the min threshold for the tier.
Note on E15: Modeled equipment is more efficient than measure tier.
Note on D16: This appears to be a typo, since code is 12.7. In reality, units that meet the requirement for two speed control of indoor fans will have IEER closer to 14.1 (as per the DEER standard baseline).
Note on H16: This is the typical IEER as-modeled; not the minimum threshold. Corresponds to 2-speed units.

## CLOSS
These curves are taken from DEER
CLossplrA |  | 0.88228 | 0.88228 | 0.88228 | 0.88228 | 0.85236 | 0.85236 | 0.85236 | 0.96409 | 0.96409 | 0.96409 | 0.96409
CLossplrB |  | 0.21053 | 0.21053 | 0.21053 | 0.21053 | 0.20333 | 0.20333 | 0.20333 | 0.28948 | 0.28948 | 0.28948 | 0.28948
CLossplrC |  | -0.04389 | -0.04389 | -0.04389 | -0.04389 | -0.04226 | -0.04226 | -0.04226 | 0.18252 | 0.18252 | 0.18252 | 0.18252
CLossplrD |  | 0.0098 | 0.0098 | 0.0098 | 0.0098 | 0.00938 | 0.00938 | 0.00938 | -0.13119 | -0.13119 | -0.13119 | -0.13119
|  | 65to134kButh | 65to134kButh | 65to134kBtuh | 65to134kBtuh | 135to239kBtuh | 135to239kBtuh | 135to239kBtuh | 240to759kBtuh-DXFG | 240to759kBtuh-DXFG | 240to759kBtuh-DXFG | 240to759kBtuh-DXFG
Measure |  | Code | Tier 1 | Tier 2 | Tier 3 | Code | Tier 1 | Tier 3 | Code | Tier 1 | Tier 2 | Tier 3
EER |  | 11 | 12.2 | 12 | 12.8 | 10.8 | 12.2 | 12 | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.2 | 14 | 16 | 19 | 12.2 | 14 | 18 | 11.4 | 12.3 | 13.1 | 14.1
| PLR | Code | Tier 1 | Tier 2 | Tier 3 | Code | Tier 1 | Tier 3 | Code | Tier 1 | Tier 2 | Tier 3
| 0.01 | 88.44% | 88.44% | 88.44% | 88.44% | 85.44% | 85.44% | 85.44% | 96.7% | 96.7% | 96.7% | 96.7%
| 0.1 | 90.29% | 90.29% | 90.29% | 90.29% | 87.23% | 87.23% | 87.23% | 99.47% | 99.47% | 99.47% | 99.47%
| 0.2 | 92.27% | 92.27% | 92.27% | 92.27% | 89.14% | 89.14% | 89.14% | 102.8% | 102.8% | 102.8% | 102.8%
| 0.3 | 94.18% | 94.18% | 94.18% | 94.18% | 90.98% | 90.98% | 90.98% | 106.4% | 106.4% | 106.4% | 106.4%
| 0.4 | 96.01% | 96.01% | 96.01% | 96.01% | 92.75% | 92.75% | 92.75% | 110.1% | 110.1% | 110.1% | 110.1%
| 0.5 | 97.78% | 97.78% | 97.78% | 97.78% | 94.46% | 94.46% | 94.46% | 113.8% | 113.8% | 113.8% | 113.8%

## EIR_fPLR
CLossplrA |  | 0 | 0 | 0 | 0.002805 | 0.01844 | 0 | 0 | 0.0080596 | 0.01843 | -2.6645e-15 | 0.010907 | -0.0052583 | -0.0018928 | 2.6306 | 0.12412
CLossplrB |  | 1 | 1 | 1 | 0.75061 | 1.1476 | 1 | 1 | 0.83829 | 1.1476 | 0.956 | 0.5652 | 0.68193 | 0.59049 | -9.5 | 0.37624
CLossplrC |  | 0 | 0 | 0 | 0.24321 | -0.20833 | 0 | 0 | 0.14651 | -0.20833 | 0.044001 | 0.42434 | 0.33272 | 0.41545 | 14.2718 | 1.2935
CLossplrD |  | 0 | 0 | 0 | 0 | 0.04227 | 0 | 0 | 0 | 0.04227 | 0 | 0 | 0 | 0 | -6.4024 | -0.79382
|  | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
Measure |  | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER | DEER VAV
| EER | 11 | 12.2 | 12 | 12.8 |  | 10.8 | 12.2 | 12 |  | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.7 | 14 | 16 | 19 |  | 12.2 | 14 | 18 |  | 11.4 | 12.3 | 13.1 | 14.1
| PLR | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER | DEER VAV
| 0.5 | 50% | 50% | 50% | 43.89% | 54.55% | 50% | 50% | 46.38% | 54.54% | 48.9% | 39.96% | 41.89% | 39.72% | 64.82% | 53.64%
| 0.6 | 60% | 60% | 60% | 54.07% | 64.11% | 60% | 60% | 56.38% | 64.11% | 58.94% | 50.28% | 52.37% | 50.2% | 68.55% | 64.4%
| 0.7 | 70% | 70% | 70% | 64.74% | 73.42% | 70% | 70% | 66.67% | 73.42% | 69.08% | 61.45% | 63.51% | 61.5% | 77.78% | 74.9%
| 0.8 | 80% | 80% | 80% | 75.89% | 82.48% | 80% | 80% | 77.25% | 82.48% | 79.3% | 73.46% | 75.32% | 73.64% | 88.65% | 84.65%
| 0.9 | 90% | 90% | 90% | 87.54% | 91.34% | 90% | 90% | 88.12% | 91.34% | 89.6% | 86.33% | 87.8% | 86.61% | 97.34% | 93.17%
| 1 | 100% | 100% | 100% | 99.66% | 100% | 100% | 100% | 99.29% | 100% | 100% | 100% | 100.9% | 100.4% | 100% | 100%

## ODFan_fPLR
OFanplrA |  | 0 | 0 | 0 | -0.002913 | 0.01844 | 0 | 0 | 0.00073097 | 0.01843 | 0 | 0 | 0 | -0.00015574 | 2.6306 | 0.12412
OFanplrB |  | 2 | 1.5152 | 2 | 0.5953 | 1.1476 | 2 | 2 | 0.67243 | 1.1476 | 2 | 3.69 | 3.5088 | 0.34955 | -9.5 | 0.37624
OFanplrC |  | 0 | 0 | 0 | 0.41127 | -0.20833 | 0 | 0 | 0.32607 | -0.20833 | 0 | 0 | 0 | 0.65091 | 14.2718 | 1.2935
OFanplrD |  | 0 | 0 | 0 | 0 | 0.04227 | 0 | 0 | 0 | 0.04227 | 0 | 0 | 0 | 0 | -6.4024 | -0.79382
|  | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
|  | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER | DEER VAV
| EER | 11 | 12.2 | 12 | 12.8 |  | 10.8 | 12.2 | 12 |  | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.7 | 14 | 16 | 19 |  | 12.2 | 14 | 18 |  | 11.4 | 12.3 | 13.1 | 14.1
| PLR | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER | DEER VAV
| 0.1 | 20% | 15.15% | 20% | 6.073% |  | 20% | 20% | 7.123% |  | 20% | 36.9% | 35.09% | 4.131% |  | 17.39%
| 0.3 | 60% | 45.45% | 60% | 21.27% |  | 60% | 60% | 23.18% |  | 60% | 100% | 100% | 16.33% |  | 33.2%
| 0.5 | 100% | 75.76% | 100% | 39.76% | 54.55% | 100% | 100% | 41.85% | 54.54% | 100% | 100% | 100% | 33.73% | 64.82% | 53.64%
| 0.7 | 100% | 100% | 100% | 61.53% | 73.42% | 100% | 100% | 63.12% | 73.42% | 100% | 100% | 100% | 56.35% | 77.78% | 74.9%
| 0.9 | 100% | 100% | 100% | 86.6% | 91.34% | 100% | 100% | 87% | 91.34% | 100% | 100% | 100% | 84.17% | 97.34% | 93.17%
| 1 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.92% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Note on H12: DEER outdoor fan is included in condensing unit, so follows the same curve as the compressor. Cycling with CLOSS below about 50% PLR.
Note on L12: DEER outdoor fan is included in condensing unit, so follows the same curve as the compressor. Cycling with CLOSS below about 50% PLR.
Note on Q12: DEER outdoor fan is included in condensing unit, so follows the same curve as the compressor. Cycling with CLOSS below about 50% PLR.

## IDFan_fPLR
FanEIRplrMin |  | 0.3 | 0.29 | 0.3 | 0.3 | 0.4 | 0.29 | 0.29 | 0.08 | 0.4 | 0.28 | 0.22 | 0.28 | 0.22 | 0.4 | 0.4
FanEIRplrMax |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
FanEIRplrA |  | -1.1189 | -1.0956 | -1.1189 | -1.1189 | -0.76471 | -1.0956 | -1.0956 | 0.2451 | -0.76471 | -1.0956 | -1.0956 | -1.0956 | 0.432 | -0.76471 | -0.76471
FanEIRplrB |  | 2.1189 | 2.0956 | 2.1189 | 2.1189 | 1.7647 | 2.0956 | 2.0956 | -1.2451 | 1.7647 | 2.0956 | 2.0956 | 2.0956 | -1.752 | 1.7647 | 1.7647
FanEIRplrC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2.32 | 0 | 0
FanEIRplrD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
| Measure | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER | DEER VAV
| EER | 11 | 12.2 | 12 | 12.8 |  | 10.8 | 12.2 | 12 |  | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.7 | 14 | 16 | 19 |  | 12.2 | 14 | 18 |  | 11.4 | 12.3 | 13.1 | 14.1
| PLR | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER | DEER VAV
| 0.1 | 30% | 29% | 30% | 30% | 40% | 29% | 29% | 14.06% | 40% | 28% | 22% | 28% | 28% | 40% | 40%
| 0.3 | 30% | 29% | 30% | 30% | 40% | 29% | 29% | 8% | 40% | 28% | 22% | 28% | 22% | 40% | 40%
| 0.5 | 30% | 29% | 30% | 30% | 40% | 29% | 29% | 12.25% | 40% | 28% | 22% | 28% | 22% | 40% | 40%
| 0.7 | 36.43% | 37.13% | 36.43% | 36.43% | 47.06% | 37.13% | 37.13% | 35.35% | 47.06% | 37.13% | 37.13% | 37.13% | 34.24% | 47.06% | 47.06%
| 0.9 | 78.81% | 79.04% | 78.81% | 78.81% | 82.35% | 79.04% | 79.04% | 74.45% | 82.35% | 79.04% | 79.04% | 79.04% | 73.44% | 82.35% | 82.35%
| 1 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## Cap_T
CoolCaptA |  | 1.8278 | 2.0979 | 1.9466 | 2.4512 | 1.9543 | 0.7961 | 1.5673 | 2.1393 | 3.5046 | 0.35974 | 1.2442 | 1.1829 | 1.9899 | 2.2459
CoolCaptB |  | -0.035147 | -0.046283 | -0.041065 | -0.053892 | -0.036502 | -0.010349 | -0.032584 | -0.047194 | -0.080819 | 0.0043726 | -0.023337 | -0.018985 | -0.042738 | -0.045908
CoolCaptC |  | 0.0003706 | 0.00052815 | 0.00048837 | 0.00062116 | 0.00035617 | 0.00012705 | 0.00042738 | 0.00052649 | 0.00080267 | 0.0001145 | 0.00036142 | 0.00027841 | 0.00050981 | 0.00051641
CoolCaptD |  | 0.0031356 | 0.0050354 | 0.0045741 | 0.0038225 | 0.0062696 | 0.0064175 | 0.0053511 | 0.0039791 | 0.00036515 | 0.0036848 | 0.003208 | 0.0024589 | 0.0036468 | 0.0026469
CoolCaptE |  | -3.3739e-05 | -1.3858e-05 | -1.3448e-05 | -1.3765e-05 | -4.1442e-05 | -6.923e-05 | -1.5432e-05 | -1.7252e-05 | 8.2232e-06 | -1.7347e-05 | -1.6563e-05 | -2.1546e-05 | -1.4924e-05 | -9.5833e-06
CoolCaptF |  | -2.0486e-05 | -0.0001135 | -0.00011051 | -0.00013631 | -5.1697e-05 | 5.3187e-05 | -0.00010622 | -8.8573e-05 | -0.00012597 | -5.7195e-05 | -7.3082e-05 | -3.2504e-05 | -9.9018e-05 | -0.00010262
|  | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
| Measure | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
| EER | 11 | 12.2 | 12 | 12.8 |  | 10.8 | 12.2 | 12 |  | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.7 | 14 | 16 | 19 |  | 12.2 | 14 | 18 |  | 11.4 | 12.3 | 13.1 | 14.1
EWB | OAT | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
60 | 95 | 0.92977 | 0.92862 | 0.92408 | 0.91577 | 0.97326 | 0.92056 | 0.91437 | 0.92041 | 0.93593 | 0.90177 | 0.88379 | 0.89989 | 0.90827 | 0.93052
63 | 95 | 0.95525 | 0.95231 | 0.9496 | 0.94445 | 0.98045 | 0.95155 | 0.94404 | 0.94786 | 0.95376 | 0.94083 | 0.92632 | 0.9364 | 0.93996 | 0.9541
67 | 95 | 0.99958 | 0.99868 | 0.99731 | 1.0001 | 1 | 0.99643 | 0.99558 | 0.9992 | 1 | 0.99613 | 0.99314 | 0.99288 | 0.99648 | 1
70 | 95 | 1.0406 | 1.0446 | 1.0433 | 1.0549 | 1.0221 | 1.0328 | 1.0432 | 1.0488 | 1.0515 | 1.04 | 1.0508 | 1.0411 | 1.0496 | 1.0453
EWB | OAT | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
67 | 85 | 1.0427 | 1.0493 | 1.0498 | 1.078 | 1.0465 | 1.0212 | 1.041 | 1.0498 | 1.0659 | 1.0288 | 1.0398 | 1.0288 | 1.0532 | 1.0595
67 | 90 | 1.022 | 1.0243 | 1.0239 | 1.0394 | 1.0243 | 1.0106 | 1.0187 | 1.0249 | 1.0328 | 1.0129 | 1.0169 | 1.0114 | 1.0252 | 1.03
67 | 95 | 0.99958 | 0.99868 | 0.99731 | 1.0001 | 1 | 0.99643 | 0.99558 | 0.9992 | 1 | 0.99613 | 0.99314 | 0.99288 | 0.99648 | 1
67 | 100 | 0.9755 | 0.97233 | 0.97004 | 0.96012 | 0.97362 | 0.97884 | 0.9717 | 0.9726 | 0.96764 | 0.97848 | 0.96855 | 0.97328 | 0.96699 | 0.96951

## SCap_T
SensCaptA |  | -0.9973 | -1.0537 | -0.94785 | -0.82778 | 0.24557 | 0.084064 | -0.37935 | 0.030265 | -4.8754 | 0.66994 | 0.69817 | -0.14712 | 0.60638 | 3.84
SensCaptB |  | 0.10518 | 0.10761 | 0.10575 | 0.11203 | 0.090507 | 0.065778 | 0.088441 | 0.077635 | 0.25179 | 0.053415 | 0.060928 | 0.086437 | 0.063787 | -0.027141
SensCaptC |  | -0.0011142 | -0.001099 | -0.0010847 | -0.0011462 | -0.0011888 | -0.00084142 | -0.0009627 | -0.00087896 | -0.0023868 | -0.00071998 | -0.0007509 | -0.0010032 | -0.00077242 | -0.00014531
SensCaptD |  | -0.0072972 | -0.007927 | -0.0081288 | -0.011259 | -0.010263 | -4.1443e-05 | -0.0071021 | -0.0080329 | -0.017726 | -0.0031537 | -0.0091246 | -0.0095767 | -0.0088485 | -0.0076466
SensCaptE |  | -3.1221e-05 | -1.4129e-05 | -1.2814e-05 | -1.5819e-05 | -4.2723e-05 | -5.9918e-05 | -1.0999e-05 | -1.301e-05 | -1.2759e-05 | -2.3319e-05 | 4.7908e-06 | -1.3435e-05 | -1.0442e-05 | -8.9167e-06
SensCaptF |  | 0.00014644 | 0.00010404 | 9.8444e-05 | 0.00010784 | 0.00021802 | 0.00013373 | 8.8251e-05 | 9.5419e-05 | 0.00023861 | 7.9075e-05 | 6.4977e-05 | 0.00014171 | 8.4366e-05 | 6.875e-05
|  | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
| Measure | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
| EER | 11 | 12.2 | 12 | 12.8 |  | 10.8 | 12.2 | 12 |  | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.7 | 14 | 16 | 19 |  | 12.2 | 14 | 18 |  | 11.4 | 12.3 | 13.1 | 14.1
EWB | OAT | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
60 | 95 | 1.162 | 1.1588 | 1.1657 | 1.1699 | 1.2783 | 1.2192 | 1.1904 | 1.1874 | 1.2007 | 1.2236 | 1.1974 | 1.2044 | 1.1989 | 1.2734
63 | 95 | 1.1081 | 1.1057 | 1.1107 | 1.1138 | 1.1733 | 1.1441 | 1.1257 | 1.1232 | 1.1433 | 1.1407 | 1.1216 | 1.134 | 1.1293 | 1.158
67 | 95 | 1.0051 | 1.0042 | 1.0071 | 1.0069 | 1 | 1.0205 | 1.0124 | 1.0129 | 1 | 1.01 | 0.99951 | 1.0119 | 1.0149 | 1
70 | 95 | 0.90442 | 0.90499 | 0.90661 | 0.90264 | 0.84505 | 0.91016 | 0.90718 | 0.91179 | 0.8424 | 0.89691 | 0.8922 | 0.89932 | 0.91282 | 0.87845
EWB | OAT | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
67 | 85 | 1.0361 | 1.0392 | 1.0455 | 1.0757 | 1.0335 | 1.0392 | 1.0441 | 1.0528 | 1.0404 | 1.0306 | 1.0386 | 1.0369 | 1.0656 | 1.0465
67 | 90 | 1.0214 | 1.0221 | 1.0266 | 1.0417 | 1.0178 | 1.0314 | 1.0285 | 1.0332 | 1.0205 | 1.0209 | 1.0189 | 1.0248 | 1.0405 | 1.0234
67 | 95 | 1.0051 | 1.0042 | 1.0071 | 1.0069 | 1 | 1.0205 | 1.0124 | 1.0129 | 1 | 1.01 | 0.99951 | 1.0119 | 1.0149 | 1
67 | 100 | 0.98722 | 0.98566 | 0.98695 | 0.9713 | 0.98007 | 1.0067 | 0.99571 | 0.99206 | 0.97887 | 0.99802 | 0.98033 | 0.99842 | 0.98871 | 0.9761

## EIR_fT
EIRtA |  | -0.32381 | -0.84828 | -0.73966 | -1.1746 | 0.13023 | 0.18282 | -0.38099 | -0.74524 | -2.0067 | 0.66919 | -1.1254 | -0.94315 | -0.62239 | -0.79627
EIRtB |  | 0.029066 | 0.046132 | 0.040001 | 0.056412 | 0.036993 | 0.01259 | 0.027315 | 0.039401 | 0.084379 | -0.0047134 | 0.055333 | 0.043256 | 0.036357 | 0.056948
EIRtC |  | -0.00016029 | -0.0003178 | -0.00026233 | -0.00034956 | -0.00027783 | -2.8413e-05 | -0.00017013 | -0.00025912 | -0.0006675 | 0.00018809 | -0.000209 | -0.00010412 | -0.00021723 | -0.00035859
EIRtD |  | -0.0027393 | -0.0024342 | -0.00096626 | -0.0042889 | -0.020132 | 0.0026234 | 0.0016291 | 0.0009393 | -0.0032537 | 0.0030347 | -0.00025661 | 0.0042137 | 0.00042774 | -0.0098866
EIRtE |  | 0.00017205 | 0.0001599 | 0.00015756 | 0.00022087 | 0.0002154 | 0.00013549 | 0.00012739 | 0.00013823 | 0.00012652 | 0.00017723 | 0.000265 | 0.00023326 | 0.00015733 | 0.000209
EIRtF |  | -0.00018637 | -0.00016061 | -0.00017054 | -0.00025355 | -6.1743e-05 | -0.00021339 | -0.00015465 | -0.00016693 | -7.588e-05 | -0.00032722 | -0.00047112 | -0.00046851 | -0.00020276 | -0.00021313
|  | 65to134kButh |  |  |  |  | 135to239kBtuh |  |  |  | 240to759kBtuh-DXFG
| Measure | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
| EER | 11 | 12.2 | 12 | 12.8 |  | 10.8 | 12.2 | 12 |  | 9.8 | 10 | 10.3 | 10.2
| IEER | 12.7 | 14 | 16 | 19 |  | 12.2 | 14 | 18 |  | 11.4 | 12.3 | 13.1 | 14.1
EWB | OAT | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
60 | 95 | 1.0733 | 1.0719 | 1.0741 | 1.0924 | 1.0291 | 1.0916 | 1.0684 | 1.0713 | 1.0532 | 1.0862 | 1.1241 | 1.1123 | 1.0818 | 1.0619
63 | 95 | 1.0482 | 1.0473 | 1.0487 | 1.0604 | 1.02 | 1.0581 | 1.0435 | 1.0463 | 1.0384 | 1.0482 | 1.0787 | 1.0701 | 1.0529 | 1.0397
67 | 95 | 1.0103 | 1.0055 | 1.0075 | 1.008 | 1 | 1.0126 | 1.0055 | 1.0057 | 1 | 1.0028 | 1.0123 | 1.011 | 1.0084 | 1
70 | 95 | 0.97848 | 0.96754 | 0.97109 | 0.96126 | 0.97919 | 0.97788 | 0.97347 | 0.96985 | 0.95717 | 0.97268 | 0.95818 | 0.96442 | 0.97037 | 0.96272
EWB | OAT | Code | Tier 1 | Tier 2 | Tier 3 | DEER | Code | Tier 1 | Tier 3 | DEER | Code | Tier 1 | Tier 2 | Tier 3 | DEER
67 | 85 | 0.85285 | 0.84966 | 0.84782 | 0.82315 | 0.85497 | 0.88545 | 0.86354 | 0.85935 | 0.85564 | 0.87265 | 0.85356 | 0.86287 | 0.85674 | 0.86546
67 | 90 | 0.92727 | 0.9236 | 0.92372 | 0.91003 | 0.9221 | 0.94564 | 0.93135 | 0.92908 | 0.92466 | 0.93328 | 0.92633 | 0.93109 | 0.92862 | 0.92751
67 | 95 | 1.0103 | 1.0055 | 1.0075 | 1.008 | 1 | 1.0126 | 1.0055 | 1.0057 | 1 | 1.0028 | 1.0123 | 1.011 | 1.0084 | 1
67 | 100 | 1.1019 | 1.0955 | 1.0992 | 1.1169 | 1.0887 | 1.0863 | 1.0861 | 1.0893 | 1.0817 | 1.0811 | 1.1116 | 1.1025 | 1.096 | 1.0829

## Savings_65to109
Measure Savings by End Use: 65 to 109 kBtu/hr Capacity
Vintage 85, CZ04, Small Office
| Annual Energy Use, kWh | [12 empty] | Savings Evaluation | [15 empty] | DEER Existing Bldg, Svgs. vs. Std
| Lights |  | Equip |  | Cooling | HtRej |  | Fans |  |  |  |  | Total | Annual Energy Savings, kWh | [6 empty] | Cool EIR |  | Cool EER |  | Fan kW/cfm |  |  | Workpaper Svgs |  | EER12, min IEER: 14.6
Std | 41784 | 0 | 58140 | 0 | 14880 | 2856 | 0 | 8221 | 0 | 0 | 0 | 0 | 125881 | Cool | HtRej | Fans | total | cool tot % annl svgs | HtRej annl % svgs | fan tot % annl svgs | 0.24111 | cool eir% | 11 | cool EER% | 0.000469 | fan pwr% | Comments | Tons | kWh/ton | Tons | kWh/ton | Individual Unit Capacities in Workpaper Model: kBtuh
Tier1 | 41784 | 0 | 58140 | 0 | 16812 | 2485 | 0 | 4843 | 0 | 0 | 0 | 0 | 124063 | -1932 | 371 | 3378 | 1817 | -12.98% | 12.99% | 41.09% | 0.22835 | 5.292% | 12.2 | 9.836% | 0.000277 | 40.94% | Fan savings dominates savings for this measure; entirely due to rated fan power | 38.0233 | 47.7864 | 36.5 | 44.1 | 68.04 | 40.35 | 34.68 | 44.38 | 30.64 | 75.09 | 42.99 | 39.11 | 47.7 | 33.3
Tier2 | 41784 | 0 | 58140 | 0 | 12264 | 3380 | 0 | 6170 | 0 | 0 | 0 | 0 | 121736 | 2616 | -524 | 2051 | 4143 | 17.58% | -18.35% | 24.95% | 0.2022 | 16.14% | 12 | 8.333% | 0.00035 | 25.37% |  | 38.0233 | 108.9594
Tier3 | 41784 | 0 | 58140 | 0 | 10797 | 994 | 0 | 4996 | 0 | 0 | 0 | 0 | 116710 | 4083 | 1862 | 3225 | 9170 | 27.44% | 65.2% | 39.23% | 0.21173 | 12.19% | 12.8 | 14.06% | 0.000283 | 39.66% | Savings for this measure significantly affected by cooling EIR, rated fan power, cooling EIR-fPLR and OD fan curve | 38.0233 | 241.1677
Note on Y8: Percent reduction in cooling implied by reduction in EIR.
Note on AA8: Percent reduction in cooling energy implied by increase in EER
Note on AC8: Pct reduction in rated fan power.

## Savings_110to239
Measure Savings by End Use: 110 to 139 kBtu/hr Capacity Range
Vintage 85, CZ04, Small Office
| Annual Energy Use, kWh | [12 empty] | Savings Evaluation | [15 empty] | DEER Existing Bdlg, Svgs. vs. Std
| Lights |  | Equip |  | Cooling | HtRej |  | Fans |  |  |  |  | Total | Annual Energy Savings, kWh | [6 empty] | Cool EIR |  | Cool EER |  | Fan kW/cfm |  |  | Workpaper Svgs |  | EER12, min IEER: 14.8
Std | 41784 | 0 | 58140 | 0 | 16032 | 3058 | 0 | 9573 | 0 | 0 | 0 | 0 | 128586 | Cool | HtRej | Fans | total | cool tot % annl svgs | HtRej annl % svgs | fan tot % annl svgs | 0.23985 | cool eir% | 10.8 | cool EER% | 0.00052617 | fan pwr% |  | Tons | kWh/ton | Tons | kWh/ton | Individual Unit Capacities in Workpaper Model: kBtuh
Tier1 | 41784 | 0 | 58140 | 0 | 14562 | 2580 | 0 | 7102 | 0 | 0 | 0 | 0 | 124167 | 1470 | 478 | 2471 | 4419 | 9.169% | 15.63% | 25.81% | 0.23386 | 2.498% | 12.2 | 11.48% | 0.00040286 | 23.44% |  | 39.4167 | 112.1099 | 37.9 | 52.1 | 70.9 | 42 | 36 | 46.3 | 30.9 | 78.3 | 44.8 | 40.7 | 49.9 | 33.2
Tier3 | 41784 | 0 | 58140 | 0 | 13797 | 856 | 0 | 1802 | 0 | 0 | 0 | 0 | 116378 | 2235 | 2202 | 7771 | 12208 | 13.94% | 72.01% | 81.18% | 0.22965 | 4.254% | 12 | 10% | 0.00016286 | 69.05% | Savings largely due to indoor fan rated power; other factors also significant | 39.4167 | 309.7167
Note on Y8: Percent reduction in cooling implied by reduction in EIR.
Note on AA8: Percent reduction in cooling energy implied by increase in EER
Note on AC8: Pct reduction in rated fan power.

## Savings_240to759
Measure Savings by End Use: 240 to 759 kBtu/hr Capacity Range
Vintage 85, CZ04, Small Office
| Annual Energy Use, kWh | [12 empty] | Savings Evaluation | [16 empty] | DEER Existing Bdlg, Svgs. vs. Std
| Lights |  | Equip |  | Cooling | HtRej |  | Fans |  |  |  |  | Total | Annual Energy Savings, kWh | [6 empty] | Cool EIR |  | Cool EER |  | Fan kW/cfm |  |  | Workpaper Svgs |  |  | EER10.8, min IEER: 12.8
Std | cool eir% | 0 | 58140 | 0 | 15520 | 2380 | 0 | 9468 | 0 | 0 | 0 | 0 | 127292 | Cool | HtRej | Fans | total | cool tot % annl svgs | HtRej annl % svgs | fan tot % annl svgs | 0.28095 | cool eir% | 9.8 | cool EER% | 0.00056069 | fan pwr% |  | Tons | kWh/ton | kWh | Tons | kWh/ton | kWh | Individual Unit Capacities in Workpaper Model: kBtuh
Tier1 | 41784 | 0 | 58140 | 0 | 11571 | 4151 | 0 | 10529 | 0 | 0 | 0 | 0 | 126175 | 3949 | -1771 | -1061 | 1117 | 25.44% | -74.41% | -11.21% | 0.24531 | 12.69% | 10 | 2% | 0.00062488 | -11.45% | Entire fan impact is due to W/cfm | 38.0233 | 29.3767 | 1117 | 48.4 | 55.4 | 2681.36 | 68.04 | 40.35 | 34.68 | 44.38 | 30.64 | 75.09 | 42.99 | 39.11 | 47.7 | 33.3
Tier2 | 41784 | 0 | 58140 | 0 | 12905 | 3461 | 0 | 5706 | 0 | 0 | 0 | 0 | 121996 | 2615 | -1081 | 3762 | 5296 | 16.85% | -45.42% | 39.73% | 0.2533 | 9.842% | 10.3 | 4.854% | 0.00033352 | 40.52% | Entire fan impact is due to W/cfm | 38.0233 | 139.2829 | 5296
Tier3 | 41784 | 0 | 58140 | 0 | 12269 | 465 | 0 | 10736 | 0 | 0 | 0 | 0 | 123395 | 3251 | 1915 | -1268 | 3898 | 20.95% | 80.46% | -13.39% | 0.25541 | 9.09% | 10.2 | 3.922% | 0.00076099 | -35.73% | Fan impact significantly affected by fan curve | 38.0233 | 102.516 | 3898
Note on C8: Percent reduction in cooling implied by reduction in EIR.
Note on Y8: Percent reduction in cooling implied by reduction in EIR.
Note on AA8: Percent reduction in cooling energy implied by increase in EER
Note on AC8: Pct reduction in rated fan power.