Work Paper SCE13CS003

Revision 2

Southern California Edison

Refrigerated Case Door Aisle Traffic Sensor

# At-a-Glance Summary

| Measure Codes | LT-74831, LT-89142 |
| --- | --- |
| Measure Description | Adding occupancy sensor-based dimming controls to a low-temperature reach-in refrigerated display case for 5 ft and 6 ft LED lighting systems. |
| Base Case Description | Low-temperature reach-in refrigerated display cases with 5 ft or 6 ft LED lighting systems, without dimming controls. |
| Units | Per door |
| Energy Savings | Refer to Excel Calculation Attachment |
| Full Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Incremental Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Effective Useful Life | 8 years (EUL_ID: ILtg-OccSens) |
| Measure Installation Type | Retrofit Add-on (REA) |
| Net-to-Gross Ratio | 0.6 (NTGR_ID: NonRes-sAll-mOccSens) |
| Important Comments | This work paper has a complementary Ex Ante Database data set that will be provided in a separate submission to the California Public Utilities Commission (CPUC). |

# Revision History

| Rev | Date | Author | Summary of Changes |
| --- | --- | --- | --- |
| 0 | 5/29/2012 | Cristalle Howe/Lincus, Inc. | - Updated workpaper format to latest template “SP&TS Work Paper Template 2013 v0.1.docx” (based upon workpaper WPSCNRCS0003) - Clarified base/measure cases and unit description - Revision to language based on code updates - Updated annual operating hours of building types according to DEER 2011 - Updated NTG values |
| 1 | 7/22/2014 | Jason Wang/SCE | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. - All savings updated using DEER 2014 operating hours and therms IEs. |
| 2 | 01/25/2016 | Ajay Wadhera/Solaris | -New template update for 2016 program year -WP effective from 1/1/2016 thru 12/31/2016 -Removed SCE building types -No value modifications |

# Commission Staff and Cal TF Comments

| Rev | Party | Submittal Date | Comment Date | Comments | WP Developer Response |
| --- | --- | --- | --- | --- | --- |

Cal TF website: http://www.caltf.org/

# Section 1. General Measure & Baseline Data

## Measure Description & Background

This work paper details the energy and demand savings associated with adding occupancy sensor-based dimming controls to a low-temperature reach-in refrigerated display case for 5 ft and 6 ft LED lighting systems. The base case is the same display case without dimming controls.

Base, Standard, and Measure Cases

| Case | Description of Typical Scenario |
| --- | --- |
| Measure | Adding occupancy sensor-based dimming controls to a low-temperature reach-in refrigerated display case for 5 ft and 6 ft LED lighting systems. |
| Existing Condition | Low-temperature reach-in refrigerated display cases with 5 ft or 6 ft LED lighting systems, without dimming controls. |
| Code/Standard | N/A |
| Industry Standard Practice | N/A |

Measures and Codes

| Measure Codes |  |  |  | Measure Name |
| --- | --- | --- | --- | --- |
| SCG | SDG&E | SCE | PG&E |  |
| N/A | N/A | LT-74831 | N/A | 5 ft LED Low Temp Reach-in Display Case Traffic Sensor Controls replacing LED Fixture with No Occupancy Sensor |
| N/A | N/A | LT-89142 | N/A | 6 ft LED Low Temp Reach-in Display Case Traffic Sensor Controls replacing LED Fixture with No Occupancy Sensor |

Measure Requirements

- Food Store are assumed to have single compressor systems, and Grocery, Retail – Single Story Large, and Retail – Multi Story Large building types are assumed to have multiplex systems for their refrigerated cases. The savings vary depending on the system, so documentation of the compressor system type (i.e. single compressor or multiplex) is required.

- Hardwired PIR and/or ultrasonic detectors must be installed to control vertically-mounted LED lighting fixtures in reach-in refrigerated display cases.

- Light levels must dim down to an established low-power mode (less than 25% of full power consumption) in less than 2 minutes when no traffic is sensed in the aisles.

## Technical Description

By reducing the percent light output of the LED lighting fixtures when there is no customer traffic, both the direct lighting energy usage as well as the refrigeration energy usage associated with the lighting load can be reduced.

The measure and base cases apply only to low-temperature “freezer” reach-in refrigerated display cases, where “freezers” are defined as having a set point temperature below 32°F.  The savings assume that the lighting systems in the refrigerated display cases operate 13.5 hours per day (based on the DEER 2014 operating hours for grocery stores) and are turned “OFF” when the facility is not operating. A facility may install occupancy sensors if they do not turn their refrigerated case lighting systems “OFF” when the facility is not operating, but, they will not get credit for the additional savings.

### LED Lighting (Baseline Technology)

Figure 1 LED Lighting for Refrigerated Display Cases

Light emitting diodes (LEDs) are solid state electronic devices.  They must be run off of DC power and require drivers for the AC to DC conversion.  If properly designed, LED lighting can offer significant savings for low temperature refrigerated display cases:

- LEDs produce visible light with little to no infrared light to produce excess heat gain compared to fluorescent [456].

- LEDs operate more efficiently at lower temperatures [227].

- LED-based lighting provides a dimming control option as an added energy savings opportunity [456]. This option is currently not available for fluorescent lighting in this application.

- LEDs have a long operating life.

### LED Lighting with dimming controls (Proposed Technology)

LED-based lighting systems offer dimming controls as an energy saving feature.  For refrigerated display case applications, dimming is accomplished via an aisle traffic occupancy sensor.  When no traffic (people) is sensed in the aisles for a specified amount of time, the light levels will dim to an established low power mode.  In theory, lighting systems may be shut off completely, but this practice may create the implication to the customers that the display case is not functioning properly. Therefore the measures in this work paper involve dimming controls only, not shut-off.

## 1.3 Installation Types and Delivery Mechanisms

The delivery mechanisms are:

- Financial Support/Down-Stream Incentive – Deemed

- Partnership/Down-Stream Incentive – Deemed.

The install type is Retrofit Add-on (REA).

Installation Type Descriptions

| Installation Type | Savings |  | Life |  |
| --- | --- | --- | --- | --- |
|  | 1st Baseline (BL) | 2nd BL | 1st BL | 2nd BL |
| Retrofit Add-on (REA) | Above Customer Existing | N/A | EUL | N/A |

A delivery mechanism is a delivery method paired with an incentive method. Delivery mechanisms are used by programs to obtain program participation and energy savings.

Delivery Method Descriptions

| Delivery Method | Description |
| --- | --- |
| Financial Support | The program motivates customers, through financial incentives such as rebates or low interest loans, to implement energy efficient measures or projects. |
| Partnership | The program implements projects through a partnership between the utility and an institutional, government, or community-based organization. |

Incentive Method Descriptions

| Incentive Method | Description |
| --- | --- |
| Down-Stream Incentive | The customer installs qualifying energy efficient equipment and submits an incentive application to the utility program. Upon application approval, the utility program pays an incentive to the customer. Such an incentive may be deemed or customized. |

## 1.4 Measure Parameters

### 1.4.1 DEER Data

DEER Difference Summary

| DEER Item | Used for Workpaper? |
| --- | --- |
| Modified DEER methodology | No |
| Scaled DEER measure | No |
| DEER Base Case | No |
| DEER Measure Case | No |
| DEER Building Types | No |
| DEER Operating Hours | No |
| DEER eQUEST Prototypes | No |
| DEER Version | N/A |
| Reason for Deviation from DEER | DEER does not contain this measure. |
| DEER Measure IDs Used | N/A |

Net-to-Gross Ratio

The NTG values were obtained using the DEER READI tool. The relevant NTG values for the measures in this work paper are in the table below.

| NTGR ID | Description | Sector | BldgType | Measure Delivery | NTGR |
| --- | --- | --- | --- | --- | --- |
| NonRes-sAll-mOccSens | Occupancy Sensors | Com | Any | PreRebDown | 0.60 |

Spillage Rate

Spillage rates are not tracked in work papers; they are tracked in an external document which will be supplied to the Commission Staff.

Installation Rate

The IR values were obtained using the DEER READI tool. The relevant IR values for the measures in this work paper are in the table below.

| GSIA ID | Description | Sector | BldgType | ProgDelivID | GSIAValue |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

Effective and Remaining Useful Life

The EUL and RUL values were obtained using the DEER READI tool. DEER defines the RUL as 1/3 of the EUL value. The RUL value is only applicable to the first baseline period for an RET measure with an applicable code baseline. The relevant EUL and RUL values for the measures in this work paper are in the table below.

| EUL ID | Description | Sector | UseCategory | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| ILtg-OccSens | Occupancy Sensors | Com | Lighting | 8 | 2.7 |

### 1.4.2 Codes and Standards Analysis

Title 24 (2013) [355] Section 120.6(b)(3) requires time switch or motion sensor controls on refrigerated display cases. The measures in this work paper are not affected by this regulation because they are REA; the base case is the customer existing equipment.

Title 20 (2014) [422] does not address lighting in refrigerated display cases.

The Code of Federal Regulations (10 CFR 431.66) has issued energy consumption standards for refrigerated display cases but does not specifically address lighting controls on display cases.

Code Summary

| Code | Reference | Effective Dates |
| --- | --- | --- |
| Title 24 (2014) | Section 120.6(b)(3) | July 1, 2014 |

## 1.5 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

### 1.5.1 Non-DEER Study Review

Several Non-DEER studies were reviewed:

- Demonstration Assessment of Lighting-Emitting Diode (LED) Freezer Case Lighting [227]: This is a DOE-sponsored study of a LED lighting and occupancy sensor retrofit of refrigerated display cases in an Albertsons store.

- LED Freezer Case Lighting Systems [456]: The Sacramento Municipal Utility District led an effort to develop an LED freezer case lighting system with motion sensors and dimming controls.

- LED Lighting for Low Temperature Refrigerated Display Cases [457]: Southern California Edison evaluated the savings potential of LEDs and aisle traffic sensors on low-temperature reach-in refrigerated display cases.

## 1.6 Data Quality and Future Data Needs

N/A

# Section 2. Calculation Methodology

Base Equations

Demand Reduction

From detailed study results with occupancy sensors, measured demand reduction is typically only 5-10% during peak periods as a result of high customer traffic during this time [457].  Because these controllers allow the LED lighting system to reach full power during peak periods, no peak demand reduction is being claimed in this work paper.

Energy Savings

Savings for occupancy sensors depend primarily on customer traffic patterns.  As such, different stores may see varying levels of savings based on their own unique customer traffic patterns.  Data from two field tests indicate that display cases incorporating occupancy sensors may operate in low power consumption mode anywhere from 15% to 30% of the time ([457] for 15%, source for 30% available upon request).  For this work paper, a conservative approach will be taken by using 15% time operation in low power mode.

Total energy savings is a combination of case lighting system energy savings and case refrigeration system energy savings associated with reduced lighting heat gains.

kWh = kWhlights + kWhrefg

Where,

kWhlights = 	The annual direct lighting energy consumption savings (kWh/door)

kWhrefg = 	The annual refrigeration system energy consumption savings associated with the reduced display case lighting heat gain (kWh/door)

Lighting Savings

Lighting energy savings is the product of average lighting power savings and runtime.  Many supermarkets and other stores turn their case lighting systems off at night when the stores are closed or when shopper traffic is light.  This will impact both the lighting and refrigeration energy use.  Since DEER 2014 operating hours are 4,910 hours/year for groceries, it is assumed that lights are turned on for 13.5 hours per day (7 days per week, 52 weeks per year).

∆kWhlights = ∆kWlights * 4,910 hours/year

Where,

∆kWlights = Lighting power savings, kW/door

For the measure case scenario, the average lighting power is a weighted average of the low and high power modes.  This weighted average is based on the % run time the case is allowed to remain in low power mode. Thus,

kWbase lights = kWhi

kWmeasure lights = 0.85 * kWhi + 0.15 * kWlo

The table below lists the lighting power ratings used for this work paper.  All values come from the manufacturer’s cutsheet (Attachment 3).

Lighting Power Values

| Lighting System | Power Hi / Lo (Watts) |
| --- | --- |
| 5’ LED Side | 13 / 8.5 |
| 5’ LED Center | 26 / 17 |
| 6’ LED Side | 16 / 11 |
| 6’ LED Center | 32 / 21 |

The lighting kW per door used in this work paper reflects the assumption of one lighting fixture per door: two side fixtures per door, or one center fixture per door.  In the case of (2) side fixtures, the lighting kW is distributed evenly between the door in question and its adjacent doors.  Therefore, the door in the analysis only uses half each fixture’s kW, but, the door has (2) side fixtures.  When the wattage for both side fixtures are combined the total kW/door is equal to the equation below:

kW/door	= kWLeft_Side + kWRight_Side

= .5*kWLeft_Side_Fixture + .5*kWRight_Side_Fixture

kW/door	= kWLeft_Side_Fixture

Where,

kW/door 	= the kW per door for both the base case or the measure case

kWLeft_Side 	= the total lighting kW on the left side of the door

kWRight_Side 	= the total lighting kW on the right side of the door

kWLeft_Side_Fixture	= the lighting fixture on the left side of the door (shared between two doors)

kWRight_Side_Fixture	= the lighting fixture on the right side of the door (shared between two doors)

kWLeft_Side_Fixture 	= kWRight_Side_Fixture

The difference in average lighting power between the base case and measure case scenarios is as follows:

∆kWlights = kWbase lights – kWmeasure lights

This simplifies to:

∆kWlights = kWhi - (0.85 * kWhi + 0.15 * kWlo)

Refrigeration Savings

The four key components of the refrigeration cycle are the evaporator, compressor, condenser, and expansion device.  The analysis of refrigeration system energy savings and demand reduction will focus primarily on the compressor, as it is the largest consuming component.  Other components are assumed to have the approximately the same consumption across the base case and measure case scenarios, and will thus cancel in the savings calculations.

Because this work paper addresses lighting for several different types of equipment with various refrigeration system configurations, compressor analysis is limited to the differential cooling load imposed by the lighting system, not the total cooling load of a particular display case.

The heat load imposed by LED display case lighting is assumed to be approximately 85% of the input power [456].

The energy efficiency ratio, or EER, as it applies to refrigeration, is a ratio of the amount of cooling provided to the amount of power input.  Through this ratio, we may determine the differential in refrigeration energy consumption between the base case and measure case scenarios.

EER = Q / kWrefg

Where,

Q 	= Cooling provided by the refrigeration system, (MBH or 1000 Btu/h)

kWrefg 	= Power input to the refrigeration system/compressor (kW)

Energy Savings Calculations

Refrigeration energy savings is the product of average refrigeration power savings and equivalent full load hours of operation (EFLH).

∆kWhrefg = ∆kWrefg * EFLH

Finding Average Power Savings

The average kW savings between the base case and measure case scenarios to meet the differential cooling load associated with lighting are as follows:

∆kWrefg = kWbase refg – kWmeasure refg

Which translates to

∆kWrefg = (∆Q / EER)

Where,

∆Q 	= k * klamp * ∆kWlights, the change in heat gain from the display case lighting across the base case and measure case scenarios (MBH)

k 	= conversion factor, 3.41 (MBH/kW)

klamp 	= LED lamp heat gain factor, 0.85

Determining EER

Analyses for two different types of refrigeration systems are included.  The first analysis focuses on smaller single-compressor systems typically seen in small convenience and grocery stores.  The second analysis deals with larger supermarket systems comprised of several multiplex compressors serving multiple refrigeration cases in the store.

- For small single compressor systems (Food Stores)

Compressor performance curves were obtained from a review of manufacturer data for small reciprocating compressors as a function of saturated condensing temperature (SCT), cooling load, and cooling capacity of compressor.  For low temperature compressors, the following equation is used to determine the EER (Btu/h/W) (Attachment 4).

EER = a + (b * SCT) + (c * PLR) + (d * SCT2) + (e * PLR2) + (f * SCT * PLR) + (g * SCT3) + (h * PLR3) + (i * SCT * PLR2) + 
(j * SCT2 * PLR)

Where,

a	= 9.86650982829017

b	= -0.230356886617629

c	= 22.905553824974

d	= 0.00218892905109218

e	= -2.48866737934442

f	= -0.248051519588758

g	= -7.57495453950879E-06

h	= 2.03606248623924

i	= -0.0214774331896676

j	= 0.000938305518020252

SCT	= Saturated Condensing Temperature (°F)

PLR	= Part Load Ratio

Where,

- The saturated condensing temperature (SCT) is the temperature at which refrigerant condenses to reject heat to ambient air.  Depending on the application, a certain temperature difference from ambient temperature is used.

  - , For low temperature (LT) applications

Where

DBadj = dry-bulb temperature (F) of ambient or adjacent space where the compressor/condensing units reside.  Defaults are based on climate zone summer design values in the table below.

ASHRAE Climate Zone Design Dry Bulb Temperature and Representative City

| CTZ | Description | Representative City | Summer Design Dry Bulb (ASHRAE Climactic Region X Data, 0.5% Column n) [°F] |
| --- | --- | --- | --- |
| 6 | South Coast | Los Angeles | 84 |
| 8 | South Coast | El Toro | 89 |
| 9 | South Inland | Pasadena | 94 |
| 10 | South Inland | Riverside | 100 |
| 11 | Central Valley | Red Bluff | 104 |
| 13 | Central Valley | Fresno | 101 |
| 14 | Desert | China Lake | 108 |
| 15 | Desert | El Centro | 111 |
| 16 | Mountain | Mount Shasta | 89 |

- Part load ratio (PLR) is the ratio of total cooling load to compressor capacity.  It indicates the percentage of compressor capacity needed to remove the cooling load.  It is calculated by following equation:

where,

PLR		= Part Load Ratio

Qcooling	= cooling load

Qcapacity	= total compressor capacity

NOTE: Compressor capacity is determined by multiplying cooling load by compressor over-sizing factor of 15%:

Qcapacity = Qcooling * 1.15

Therefore, PLR = 1/1.15 = 0.87

Typically, reduction in cooling load results in a decreased EER for a retrofit measure due to a change in the PLR.  However, this analysis deals with the change in cooling load for many different sizes of equipment in multiple applications with varying baseline cooling loads. Therefore, it would be difficult to assume a new PLR that would be applicable to all types of equipment addressed here.  To simplify the analysis, EER is assumed to remain constant for both the baseline and retrofit situations.

- For large multiplex compressor systems (Grocery Stores and Large Retail)

Compressor performance curves were obtained from a review of manufacturer data for large reciprocating compressors as a function of saturated condensing temperature (SCT) and saturated evaporator temperature (SET). In multiplex systems, suction pressure controls ensure SET remains constant, so no PLR analysis is necessary.  For low temperature compressors, the following equation is used to determine the EER (Btu/h/W) (Attachment 5).

EER = a * SCT3 + b * SCT2 + c * SCT + d

Where,

a	= 0.00000491

b	= -0.00107023

c	= -0.03013591

d	= 15.74788397

SCT	=Saturated Condensing Temperature (°F)

This analysis also assumes no change in EER due to a reduction in cooling load for a retrofit measure.

Equivalent full load hours (EFLH) of operation

EFLH is determined by multiplying annual available operation hours, H, by overall duty cycle factor.  Duty cycle is a function of compressor capacity, defrost and weather, as shown below.

The following equation shows the relationship between capacities, defrost and weather factor.

Duty cycle = Capacity factor x Defrost factor x Weather factor

Where,

Capacity factor 	= function of PLR, (1-PLR)

Defrost factor 	= N/A (value of 1)

Weather factor 	= function of CTZ (see discussion below)

Capacity factor is a function of compressor capacity and cooling load, determined by subtracting the PLR from 1.  As shown above, a compressor over-sizing factor of 15% results in a PLR of 87%. A PLR of 87% equates to a capacity factor of (1-87%) or 13%.

The defrost factor depends on the number and duration of defrost cycles and is determined by dividing the defrost duration (in hours) by 24 hours.  However, defrost cycles typically occur at night during store off hours when display case lighting is shut off.  The energy required to meet the differential cooling from lighting is not captured during the defrost time period so defrost factor will not be used in this work paper.

Weather factor is a function of CTZ.  Using DOE-2 simulation results for a typical supermarket, weather factors were determined for each CTZ.

To estimate weather factor for each CTZ, the annual energy usage of a refrigeration system for a typical supermarket in each CTZ, based on a DOE-2 computer simulation, was used [251].  Using CTZ 15 as a benchmark with 85% weather factor, weather factors for the other 7 SCE CTZs were estimated.  The table below illustrates the annual energy usage of refrigeration for each SCE CTZ and corresponding weather factors.  The following equation shows the methodology.

WFCTZ,X = Annual kWh CTZXAnnaul kWh CTZ15* WFCTZ-15

Where,

WFCTZ,X	= weather factor for each CTZ (i.e. CTZ 6)

Annual kWh CTZX	= annual energy usage of refrigeration system for each individual CTZ, kWh/yr

Annual kWh CTZ15	= annual energy usage of refrigeration system for CTZ 15, kWh/yr

WFCTZ-15	= weather factor for CTZ 15, 85%

Weather Factor Values for All SCE Climate Zones

| CTZ | Refrigeration Annual Energy Usage (kWh/yr) | Weather Factor (%) |
| --- | --- | --- |
| 6 | 502,982 | 78.9% |
| 8 | 506,024 | 79.4% |
| 9 | 500,936 | 78.6% |
| 10 | 495,565 | 77.7% |
| 13 | 496,488 | 77.9% |
| 14 | 491,056 | 77.0% |
| 15 | 541,873 | 85.0% |
| 16 | 452,877 | 71.0% |

Accordingly, EFLH = 4,910 x Duty cycle (hrs/yr) or EFLH = 4,173.50 x WFCTZ,X

Therm Savings Calculations

The therm savings will be realized in the room where the refrigeration equipment is housed.  The refrigeration equipment will eject less heat because the heat input from the lighting system will be decreased.  Therefore, the HVAC system of that room will need to provide additional heating to the building (hence negative therms).  On single compressor systems, the heat is rejected into the conditioned space below the refrigerated case (Attachment 6).  On multiplex systems, the heat is rejected in an air cooled or water cooled condenser which is typically outside.  Therefore, there will be no therm savings on multiplex systems since their heat rejection equipment is not located in a conditioned space.

DEER provides interactive effects values for kW, kWh, and therms based on the building type and climate zone.  Interactive effects values are dimensionless units which quantify the HVAC savings when lighting loads are decreased in conditioned spaces.  The interactive effects values were obtained from DEER 2014.  The equation to find the therm savings is as follows:

Therm Savings = ΔkWh * Therm IE FactorCTZ,Building Type

Where,

Therm IE FactorCTZ,Building Type = therms interactive effect factor based on the climate zone and building type.

Energy savings values are reported per door.  No further normalization is required.

Example Calculation

An example calculation for an occupancy sensor is shown below.  The table below summarizes the measure information used for a 5’ LED lamp in a Grocery Store in climate zone 6.

Example Occupancy Sensor Calculation Permutation Information

| Length of LED | Building Type | CTZ | kWhi | kWlo |
| --- | --- | --- | --- | --- |
| 5’ | Grocery Store | 6 | .026 | .017 |

Lighting Savings:

Baseline and Measure Case Energy Calculation

kW/doorbaselights 	= kWhi

= .026

kW/doormeasurelights 	  = .85*kWhi + .15*kWlo

= .85*.026 + .15*.017

= .02465

Average kW Savings:

ΔkWlights = 	kWbase lights – kWmeasure lights

= .026 – .02465

ΔkWlights = .00135

kWh Savings

ΔkWhlights = ΔkWlights * 4,910 hours/year

= .00135 * 4,910

ΔkWhlights = 6.63

Refrigeration 	Savings:

Cooling Load Savings:

ΔQ = k*klamp*ΔkWlights

= 3.41214 * .85*.00135

ΔQ = .00392

Compressor EER:

EER = a*SCT3 + b*SCT2 + c*SCT + d

= .00000491*(94)3 + (-00107023)*(94)2 + (-0.03013591)*(94) + 15.74788397

EER	= 7.53672

kW Savings

ΔkW =(ΔQ/EER)

= .00392/7.53672

ΔkW = .00052

Weather Factor

WFCZ= Annual kWh CTZ6Annual kWh CTZ15x WFCTZ-15

= (502,982/541,873) x 85%

WFCZ = 78.9%

Duty Cycle

Duty Cycle = Capacity Factor * Defrost Factor * Weather Factor

= .85*1*.789

Duty Cycle = .67065

Equivalent Full Load Operating Hours

ELFH = 4,910 X Duty Cycle

= 4,173.50 x WFCTZ,6

= 4,173.50 x .789

ELFH = 3,292.9

kWh Savings

ΔkWhrefg = ΔkWrefg * EFLH

= .0052 * 3,292.9

ΔkWhrefg = 1.71070

Total Savings:

kWh Savings

ΔkWh = ΔkWhlights + ΔkWhRefg

= 6.63 + 1.71070

ΔkWh = 8.34

Therm Savings/Penalty

Therms savings are not applicable for the “Grocery Store” building type since this building type has multiplex compressor systems.

The tables below summarize the energy savings and therm savings of occupancy sensors on 5’ and 6’ LED lighting systems for LT applications for all 16 climate zones in small stores and supermarkets respectively.  The calculations can be found in Attachment 2.

Energy Savings Summary

| Annual Energy Savings (∆kWh) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Climate Zone | Representative City and Temperature | Measure Unit | Small Store (Food Stores) |  | Large Store (Grocery Stores and Large Retail Stores) |  |
|  | (Summer Design Dry-Bulb, ASHRAE Climatic Region X Data, 0.5% Column) |  | Occ Sensors, 5' LED | Occ Sensors, 6' LED | Occ Sensors, 5' LED | Occ Sensors, 6' LED |
| 6 | Los Angeles - 84 °F | Per door | 8.76 | 10.71 | 8.34 | 10.19 |
| 8 | El Toro - 89 °F | Per door | 8.96 | 10.95 | 8.47 | 10.35 |
| 9 | Pasadena - 94 °F | Per door | 9.13 | 11.15 | 8.59 | 10.49 |
| 10 | Riverside - 100 °F | Per door | 9.35 | 11.43 | 8.74 | 10.68 |
| 13 | Fresno - 101 °F | Per door | 9.40 | 11.49 | 8.77 | 10.72 |
| 14 | China Lake - 108 °F | Per door | 9.71 | 11.87 | 8.98 | 10.97 |
| 15 | El Centro - 111 °F | Per door | 10.21 | 12.48 | 9.34 | 11.41 |
| 16 | Mount Shasta - 89 °F | Per door | 8.71 | 10.65 | 8.28 | 10.12 |

Therm Savings Summary

| Annual Therm Savings (∆Therm) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Climate Zone | Representative City and Temperature | Measure Unit | Small Store (Food Stores) |  | Large Store (Grocery Stores and Large Retail Stores) |  |
|  | (Summer Design Dry-Bulb, ASHRAE Climatic Region X Data, 0.5% Column) |  | Occ Sensors, 5' LED | Occ Sensors, 6' LED | Occ Sensors, 5' LED | Occ Sensors, 6' LED |
| 6 | Los Angeles - 84 °F | Per door | -0.11295 | -0.10444 | 0 | 0 |
| 8 | El Toro - 89 °F | Per door | -0.10379 | -0.09389 | 0 | 0 |
| 9 | Pasadena - 94 °F | Per door | -0.10390 | -0.09224 | 0 | 0 |
| 10 | Riverside - 100 °F | Per door | -0.10379 | -0.08993 | 0 | 0 |
| 13 | Fresno - 101 °F | Per door | -0.10704 | -0.09224 | 0 | 0 |
| 14 | China Lake - 108 °F | Per door | -0.11449 | -0.09553 | 0 | 0 |
| 15 | El Centro - 111 °F | Per door | -0.06363 | -0.05049 | 0 | 0 |
| 16 | Mount Shasta - 89 °F | Per door | -0.13836 | -0.12870 | 0 | 0 |

All calculations are in Attachment 2, and a complete list of savings is in Attachment 1.

# Section 3. Load Shapes

The ideal load shape for net benefits estimates would represent the difference between the base case and measure case. The closest load shapes that are applicable to the measures in this work paper are listed in the table below.

Building Types and Load Shapes

| Building Type | Load Shape | E3 Alternate Building Type |
| --- | --- | --- |
| Grocery | Occupancy Sensor | Misc._Commerical |
| Retail - Multistory Large | Occupancy Sensor | Large_Retail_Store |
| Retail - Single-Story Large | Occupancy Sensor | Large_Retail_Store |

# Section 4. Costs

## 4.1 Base Case Cost

For REA measures, the base case cost is zero.

## 4.2 Measure Case Cost

The costs of the LED occupancy sensors vary depending on manufacturer.  The costs have been calculated per door of refrigerated display case as seen below and are based on data from a field test conducted by SCE (available upon request).

Measure Cost Information

| Description | Cost |
| --- | --- |
| Equipment Cost (per sensor) | $50 |
| Sensors per Door (14 sensors/125 doors = 0.1) | 0.1 |
| Per door costs: |  |
| Equipment Cost (per door) | $5 |
| Labor Cost (per door) | $41 |
| Full Measure Cost | $46 |

## 4.3 Full and Incremental Measure Cost

For REA measures, the incremental measure cost is the same as the gross measure cost shown in section 4.2

Full and Incremental Measure Cost Equations

| Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- |
|  |  | 1st Baseline | 2nd Baseline |
| REA | MEC + MLC | MEC + MLC | N/A |

MEC = Measure Equipment Cost; MLC = Measure Labor Cost

BEC = Base Case Equipment Cost; BLC = Base Case Labor Cost

Full and Incremental Costs

| Measure | Installation Type | Incremental Measure Cost | Full Measure Cost |  |
| --- | --- | --- | --- | --- |
|  |  |  | 1st Baseline | 2nd Baseline |
| 5 ft LED Low Temp Reach-in Display Case Traffic Sensor Controls replacing LED Fixture with No Occupancy Sensor | REA | $46 | $46 | N/A |
| 6 ft LED Low Temp Reach-in Display Case Traffic Sensor Controls replacing LED Fixture with No Occupancy Sensor | REA | $46 | $46 | N/A |

# Attachments

# References

| [227] | Demonstration Assessment of Lighting-Emitting Diode (LED) Freezer Case Lighting |
| --- | --- |
| [251] | New Refrigeration Measure Computer Simulation Report |
| [355] | 2013 Building Energy Efficiency Standards for Residential and Nonresidential Buildings (Title 24) |
| [422] | 2014 Appliance Efficiency Regulations (Title 20) |
| [456] | LED Freezer Case Lighting Systems |
| [457] | LED Lighting for Low Temperature Refrigerated Display Cases |