## Key
This workbook was used to develop piping layouts and unit sizing for VRF systems for specific building types.
Values for some activity areas are referenced to other building types in this workbook.
Area | Floor area for this activity area in the prototype model.
% Area | Percent of total floor area for this activity area.
Area/ ODU | Target floor area per outdoor unit.
Len | Length of typical building area served by one VRF system
Depth | Depth of typical building area served by one VRF system
Max ton/sys | Maximum tons per system used by DOE2 to determine minimum number of systems. Sometimes set larger than TypTon/sys to prevent division into a larger number of significantly smaller systems. More systems increases piping losses in the model.
Typ ton/sys | This is the typical installed outdoor unit capacity. It is used here to determine the rated EIR and rated SST and SDT.
appx ODU sf/ton | This is a check on whether the area/ODU and ton/sys values are reasonable. Typically sf/ton is on the order of 300 to 400. Lower for high load spaces such as kitchens and computer rooms.
Ldr | Length of pipe from unit to first branch.
Hdr | Length of pipe from first branch to last branch; includes elevation change component.
Nom Hdr Ht | The nominal elevation change of the header, typically not including floor-to-floor changes.
Perim Brn L | Length of branch for perimeter zones
Core Branch L | Length of branch for core zones
Trg area/IDU | This is used along with zone area to calculate the number of indoor units input into DOE2. The calculated value will be recalculated by DOE2 if the Max Ton/IDU is violated.
Max Ton/IDU | If the indoor unit capacity exceeds this value, then VRF-NUM-UNITS will be recalculated by DOE2 to the nearest integer that satisfies this maximum.
Num IDUs | Set to -99 to calc in worksheet based on Trg area/unit. The calculated value will be assigned to the keyword VRF-NUM-UNITS. Set to "1" to allow DOE2 to calc based on Max Ton/IDU.
IDU Config | Indoor unit configuration: Ducted, Surface or Mixed

## OfS
|  | L | D | A | Tons
| Office | 213.5503 | 15 | 3203.2542 | 9.1522 |  |  | Model has 2 floors, each at 5,000 sq ft
| Lobby | 12.5213 | 20 | 250.4265 | 0.7155 |  |  | Assume heat recovery VRF has one system per floor, 14 tons/system
| Waiting | 12.5213 | 20 | 250.4265 | 0.7155 |  |  |  | Model as two systems per floor to handle two trunks per floor
| Circulation | 85.4119 | 5 | 427.0597 | 1.2202 |  |  | Assume heat pump VRF also has 2 systems per building at 14 tons/system
| Toilets | 10.6804 | 20 | 213.6084 | 0.61031 |  |  |  | Model as one system per orientation in order to minimize unmet loads
| Conference | 8.5443 | 20 | 170.8867 | 0.48825 |  |  |  |  | Five systems in model/ each at about 6 tons
| Mech/elec | 20.0022 | 20 | 400.0446 | 1.143 | [5 empty] | This will make five pipe runs instead of the desired two
| Copy | 8.5443 | 10 | 85.4434 | 0.24412 | [6 empty] | Handle the difference by making the trunk lengths shorter:
Small Office Building | Total |  |  | 5001.15 | 14.289 | [7 empty] | Ldr: |  | 10
[5 empty] | 28.578 | [7 empty] | Hdr: |  | 28
425
35.4167
Small office piping summary
| Trunk | Ldr | Hdr | Brn1 | Brn2 | Brn3 | Brn4 | Brn5 | Brn6 | Brn7 | Brn8
| T1 | 25 | 75 | 10 | 10 | 15 | 15 | 10 | 15
| T2 | 25 | 65 | 15 | 10 | 25 | 7 | 15 | 20 | 15 | 25
| Average | 25 | 70 | Brn1: 14.7857
Model Indoor units
| Area | Qty |  | Brn1: Area/unit; Brn3: Approx Tons/Unit
| 5001 | 11 |  | Brn1: 454.6364; Brn3: 1.299
|  | Act Area |  | Area | % Area | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | appx ODU sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Branch L | Trg area/IDU | Max Ton/IDU | Num IDUs | IDU Config | Geometry reference
|  | Any |  | 5000 | 1 | 5000 | 85 | 60 | 16 | 14 | 357.1429 | 25 | 70 | -10 | 15 | 15 | 450 | 1.5 | -99 | MIXED | Diagram
ODU
Office
Office
Office
Office
Conf/Copy
Circ
Mech/ Elec
Toilets
Lobby/ waiting
Trunk1
Trunk2
85 ft
60 ft
Note on BC29: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on BH29: -99 = Calc in worksheet 1 = calc in DOE2

## OfL
Approx
Large Office Building |  |  |  |  | L | D | A | Tons
|  |  |  | One Sys | 81 | 108 | 8748 | 24.9943
Two systems per floor
3 compressors per system
|  | Leader | 20 | ft | Vertical:
|  | Header | 65 | ft | 20 ft
|  | Pvt office | 25 | ft | 0
|  | Open Office | 45 | ft | 0 | ft
[9 empty] | Act Area | Area | % Area | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | appx ODU sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Branch L | Trg area/IDU | Max Ton/IDU | Num IDUs | IDU Config | Geometry reference
[9 empty] | Any | 17496 | 1 | 8748 | 81 | 108 | 24 | 20 | 364.5 | 20 | 65 | 3 | 50 | 30 | 1500 | 3 | 1 | MIXED | Diagram
Large Office Building
162 ft
108 ft
25 ft
45 ft
65 ft
ODU
ODU
Note on BQ14: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on BV14: -99 = Calc in worksheet 1 = calc in DOE2

## EPr
Summary for Primary School
Primary School | [9 empty] | Piping Length, ft
[8 empty] | Activity Area | System Tons | Outdoor Trunk | Indoor Header | Branch | Sq ft per indoor unit | Act Area | Area | % Area | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | appx ODU sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Branch L | Trg area/IDU | Max Ton/IDU | Num IDUs | IDU Config | Geometry reference
[8 empty] | Classroom | 18 | 15 | 70 | 20 | 900 | Classroom | [5 empty] | 22 | 18 |  | 15 | 70 | 3 | 25 | 25 | 900 | 3.5 | -99 | SURFACE | Diagram
[8 empty] | Gymnasium | 18 | 15 | 60 | 15 | 1500 | Cafeteria | [5 empty] | 22 | 18 |  | 15 | 80 | 3 | 20 | 20 | 1000 | 3.5 | -99 | SURFACE | Diagram
|  | Pipe lengths: | Plan | Effective |  | Vertical: |  | Dining/Kitchen | 18 | 15 | 80 | 15 | 916.6667 | Gymnasium | [5 empty] | 22 | 18 |  | 15 | 60 | 3 | 20 | 20 | 1500 | 5.5 | -99 | DUCTED | Diagram
|  | Leader | 15 | 20 | ft | 6 | [7 empty] | Kitchen | [5 empty] | 22 | 18 |  | 15 | 80 | 3 | 20 | 20 | 900 | 6 | -99 | DUCTED | Diagram
|  | Header | 70 | 75 | ft | 0 | ft
|  | Branch | 20 | 25 | ft | 0 | ft
Approx
|  |  | L | D | A | Tons
|  | CL wing | 90 | 66 | 5940 | 16.9714
|  | Gym | 120 | 50 | 6000 | 17.1429
|  | Cafe/KT | 110 | 50 | 5500 | 15.7143
Classroom wing
|  | Pipe lengths: | Plan | Effective
|  | Leader | 15 | 20 | ft
|  | Header | 60 | 65 | ft
|  | Branch | 15 | 20 | ft
Gymnasium
|  | Pipe lengths: | Plan | Effective
|  | Leader | 15 | 20 | ft
|  | Header | 80 | 85 | ft
|  | Branch | 15 | 20 | ft
CZ15
CZ16
Cafeteria/Kitchen
90 ft
66 ft
20 ft
ODU
120 ft
50 ft
ODU
110 ft
50 ft
ODU
70 ft
Note on BL4: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on BQ4: -99 = Calc in worksheet 1 = calc in DOE2

## Htl
[13 empty] | Piping Length, ft |  |  | Indoor Units
[11 empty] | Activity Area | System Tons | Outdoor Trunk | Indoor Header | Branch | Sq ft/unit | Typ. ton/ unit | Act Area | Area | % Area | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | appx ODU sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Branch L | Trg area/IDU | Max Ton/IDU | Num IDUs | IDU Config | Geometry reference
| Hotel | [9 empty] | Guest Room - top | 8 | 30 | 60 | 10 | 288 | 0.82286 | Laundry | [5 empty] | 22 | 18 |  | 50 | 60 | -10 | 20 | 20 | 2000 | 6 | -99 | DUCTED | Diagram
[11 empty] | Guest Room - mid | 8 | 30 | 120 | 10 | 288 | 0.82286 | HotelLobby | [5 empty] | 22 | 18 |  | 50 | 60 | -10 | 20 | 20 | 1000 | 4 | -99 | DUCTED | Diagram
[11 empty] | Guest Room - lower | 8 | 30 | 180 | 10 | 288 | 0.82286 | OfficeGeneral | [5 empty] | 22 | 18 |  | 50 | 60 | -10 | 20 | 20 | 1000 | 4 | -99 | DUCTED | Diagram
[11 empty] | Public areas | 18 | 50 | 70 | 30 | 1050 | 3 | BarCasino | [5 empty] | 22 | 18 |  | 50 | 60 | -10 | 20 | 20 | 2000 | 4 | 1 | DUCTED | Diagram
[11 empty] | Kitchen | 18 | 50 | 70 | 30 | 1050 | 3 | Dining | [5 empty] | 22 | 18 |  | 50 | 60 | -10 | 20 | 20 | 1000 | 4 | 1 | DUCTED | Diagram
|  | Pipe lengths: | Plan | Effective |  | Vertical: | [11 empty] | GuestRmCorrid | [5 empty] | 22 | 18 |  | 30 | 60 | 5 | 10 | 10 | 1000 | 2.6 | -99 | DUCTED | Diagram
|  | Leader | 10 | 15 | ft | varies | [6 empty] | ton/sys | rms/sys | ton/rm |  |  | Kitchen | [5 empty] | 22 | 18 |  | 50 | 60 | -10 | 20 | 20 | 1000 | 5 | 1 | DUCTED | Diagram
|  | Header | 130 | 143 | ft | 0 | ft | [5 empty] | 6 | 10 | 0.6 |  |  | GuestRmOcc | [5 empty] | 8 | 8 |  | 30 | 60 | 5 | 10 | 10 | 288 | 2 | -99 | SURFACE | Diagram
|  | Branch | 15 | 20 | ft | 0 | ft | [5 empty] | 8 | 12 | 0.66667 | 392 |  | GuestRmUnOcc | [5 empty] | 8 | 8 |  | 30 | 60 | 5 | 10 | 10 | 288 | 2 | -99 | SURFACE | Diagram
276
Add larger of 5 ft or 10% for fittings and bends
Approx
[9 empty] | L | D | A | Tons | ton/sys | rms/sys | ton/rm
[8 empty] | Guest wing | 144 | 54 | 7776 | 22.2171 | 8 | 12 | 0.66667
[8 empty] | Laundry/bar | 100 | 54 | 5400 | 15.4286
[8 empty] | Kitchen | 27.7778 | 54 | 1500 | 7.5
8000
Guest room wing
|  | Pipe lengths: | Plan | Effective
|  | Leader | 10 | 15 | ft
|  | Header | 80 | 88 | ft
|  | Branch | 15 | 20 | ft
Public Areas
144 ft
54 ft
ODU
100 ft
80 ft
25 ft
ODU
ODU

## Asm
Assembly | [6 empty] | ODU Capacity | [7 empty] | IDU Capacity
ActArea | Layout | Area | % Area | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | appx ODU sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Branch L | Trg area/IDU | Max Ton/IDU | Num IDUs | IDU Config | Geometry reference
Auditorium |  | 26039.6 | 76.58% | 12000 | 66.6667 | 180 | 36 | 30 | 400 | 20 | 140 | 5 | 27 | 27 | NA | 7 | 1 | Ducted | Diagram below
OfficeGeneral |  | 7963.76 | 23.42% | 3981.88 | 50 | 79.6376 | 8 | 14 | 284.42 | 25 | 65 | 5 | 15 | 15 | NA | 1.5 | 1 | Mixed | Small office building
For heat recovery VRF, use one system for auditorium and one for the office/general
For heat pump VRF, use one system per zone
|  |  |  | 10.5 |  |  | Area/per
|  |  |  | 350 |  |  | Btu/per
|  |  |  | 33.3333 |  |  | Btu/sf
|  |  |  | 360 |  |  | sf/ton
180 ft
145 ft
ODU
ODU
ODU
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on S3: -99 = Calc in worksheet 1 = calc in DOE2
Note on I5: Max ton/sys is set to slightly above half of unit size in order to split the system and model two main trunks per floor.

## ESe
Secondary School |  | Area | % Area |  |  |  | ODU Capacity
Total | Model has four 2-story bldgs w/ 1 gym bldg | 149994.212 | 1 | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | appx ODU sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Brn L | Trg area/unit | Max Ton/IDU | Num IDUs | IDU Config | Geometry reference | Stories | Vertical
Classroom | Same footprint as EPr | 88201.44 | 58.8% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 15 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Surface | Same as primary school classroom | 2 | 5 or 17
Cafeteria | Similar to CL | 22490.2 | 14.99% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 15 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Ducted | Same as classroom | lwr | 5
Kitchen | Separate system, 1st flr only | 10502.16 | 7.002% | 4000 | 80 | 50 | 22 | 18 | 222.2222 | 15 | 70 | 3 | 25 | 25 | 1000 | 6 | 1 | Ducted | Same as classroom | lwr | 5
OfficeGeneral | Like small office; includes msc spaces | 3218.04 | 2.145% | 5000 | 83.3333 | 60 | 8 | 14 | 357.1429 | 25 | 63 | 3 | 15 | 15 | 500 | 1.5 | 1 | Mixed | Same as small office building | 2 | 5 | Equip | Ppl
CompRoomClassrm | Group with classroom in VRF layout | 3082.372 | 2.055% | 5000 | 74.9625 | 66.7 | 22 | 18 | 277.7778 | 15 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Surface | Same as classroom | 2 | 5 | 19.1128 | 5.3333 | 490.8752 | 13.3333 | 2.25
Gymnasium | Same footprint as EPr | 22500 | 15% | 6000 | 120 | 50 | 22 | 18 | 333.3333 | 15 | 60 | 3 | 20 | 20 | 1500 | 5.5 | 1 | Ducted | Same as EPr gym | 1 | 5
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.

## ECC
Community College | [6 empty] | ODU Capacity
Overall | Two identical rotated bldgs | 300045.7 |  | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | approx sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Brn L | Trg area/unit | Max Ton/IDU | Num IDUs | IDU Config | Goemetry reference | Stories | Vertical
Cafeteria | Same as classroom | 26257.6 | 8.751% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 20 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Ducted | Same as classroom | lwr
Classroom | Same as other schools | 150851.436 | 50.28% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 20 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Surface | Based on primary school | 3
CompRoomClassrm | Group with classrooms | 9589 | 3.196% | 5000 | 74.9625 | 66.7 | 22 | 18 | 277.7778 | 20 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Surface | Same as classroom | 3
IndLowBay | Shop classrooms, labs | 37493 | 12.5% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 20 | 70 | 3 | 25 | 25 | 900 | 3.5 | 1 | Surface | Same as classroom | lwr
Kitchen |  | 5625.42 | 1.875% | 6000 | 89.955 | 66.7 | 22 | 18 | 333.3333 | 20 | 40 | 3 | 25 | 25 | 1000 | 6 | 1 | Ducted | Stand-alone system | lwr
OfficeGeneral | Like small office | 70229.244 | 23.41% | 5000 | 83.3333 | 60 | 8 | 14 | 357.1429 | 20 | 65 | 3 | 50 | 30 | 1500 | 3 | 1 | MIXED | Large office building | 3
Zoning for Heat Recovery VRF
| CondUnit1 | Shop classrooms
| CondUnit2 | All other classrooms and office areas
| CondUnit3 | Cafeteria and Kitchen
Zoning for Heat Pump VRF
| CondUnit1 | Shop classrooms
| CondUnit2 | West classrooms
| CondUnit3 | South classrooms
| CondUnit4 | North Classrooms
| CondUnit5 | Cafeterias
| CondUnit6 | East classrooms
| CondUnit7 | Core offices
| CondUnit8 | Kitchens
| CondUnit9 | Computer classrooms
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.

## EUn
University | [6 empty] | ODU Capacity
|  | 470866.863 |  | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | approx sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Brn L | Trg area/unit | Max Ton/IDU | Num IDUs | IDU Config | Goemetry reference | Stories | Vertical
Cafeteria | Same as classroom | 24010.8 | 2.401% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 20 | 70 | 5 | 25 | 25 | 900 | 3.5 | 1 | Ducted | Primary school cafeteria | 1 | 5
Classroom | Same as other schools | 402878.683 | 40.29% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 20 | 70 | 5 | 25 | 25 | 900 | 3.5 | 1 | Surface | Primary school classroom wing | 4 | 24
CompRoomClassrm | Group with classrooms | 38007.54 | 3.801% | 5000 | 74.9625 | 66.7 | 22 | 18 | 277.7778 | 20 | 70 | 5 | 25 | 25 | 900 | 3.5 | 1 | Surface | Classroom | 4 | 24
CorridorStairway | Dorm only: similar to hotel guest room corridor | 29980.64 | 2.999% | 2250 | 150 | 6 | 14 | 10 | 225 | 20 | 60 | 5 | 10 | 10 | 1125 | 2 | -99 | Ducted | Hotel gest room corridor | 5 | 24 | Set at two per floor and let ton/IDU float
DormitoryRoom | Typical wing is 38 x 150; one room is 12 x 16; 5 stories | 169889.6 | 16.99% | 2048 | 72 | 38 | 8 | 8 | 256 | 20 | 60 | 5 | 10 | 10 | 192 | 0.75 | -99 | Surface | Hotel guest room | 5 | 24 | Set at one IDU /room and let Ton/IDU float
IndLowBay | Labs and shop classrooms | 80004 | 8.002% | 6000 | 90 | 66.6667 | 22 | 18 | 333.3333 | 20 | 70 | 5 | 25 | 25 | 900 | 3.5 | 1 | Ducted | Primary school classroom wing | 1 | 5
Kitchen | Separate system | 10487.94 | 1.049% | 6000 | 89.955 | 66.7 | 22 | 18 | 333.3333 | 20 | 40 | 5 | 25 | 25 | 900 | 6 | 1 | Ducted | Stand-alone system | 1 | 5
OfficeGeneral | Same as large office | 244578.477 | 24.46% | 5000 | 83.3333 | 60 | 24 | 20 | 250 | 20 | 65 | 5 | 50 | 30 | 1500 | 3 | 1 | Mixed | Large Office | 4 | 24
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on S3: Set to -99 to calc in worksheet based on Trg area/unit. Set to "1" to allow DOE2 to calc based on Max Ton/IDU.

## Nrs
Nursing Home | [6 empty] | ODU Capacity
|  |  |  | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | approx sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Brn L | Trg area/unit | Max Ton/IDU | Num IDUs | IDU Config | Goemetry reference | Stories | Vertical
Dining |  | 12594.08 | 10.5% | 6297.04 | 130 | 48.4388 | 24 | 20 | 314.852 | 20 | 75 | 3 | 35 | 35 | 1000 | 3.5 | 1 | Ducted | Stand-alone system | 2
Kitchen |  | 5398.24 | 4.499% | 5398.24 | 75 | 71.9765 | 24 | 20 | 269.912 | 20 | 75 | 3 | 35 | 35 | 1000 | 3.5 | 1 | Ducted | Stand-alone system | 2
OfficeGeneral | Support in 100 x 140 ft wing | 29986.22 | 24.99% | 7000 | 140 | 50 | 24 | 20 | 350 | 20 | 100 | 3 | 40 | 20 | 1500 | 3.5 | 1 | MIXED | Nursing home building | 2
FacMaint | Support in 100 x 140 ft wing | 11998.48 | 10% | 7000 | 140 | 50 | 24 | 20 | 350 | 20 | 100 | 3 | 40 | 20 | 1500 | 3.5 | 1 | Ducted | Nursing home building | 2
PatientRoom | One wing is 100 ft long | 53348.8 | 44.46% | 2400 | 52.1739 | 46 | 8 | 8 | 300 | 20 | 40 | 3 | 15 | 15 | 240 | 0.75 | -99 | Surface | Hotel guest room | 2
CorridorStairway | Assume 4 corridors, each 100 ft | 6656.08 | 5.548% | 2304 | 384 | 6 | 8 | 8 | 288 | 20 | 80 | 3 | 10 | 10 | 1000 | 2 | -99 | Ducted | Hotel corridor | 2
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on S3: Set to -99 to calc in worksheet based on Trg area/unit. Set to "1" to allow DOE2 to calc based on Max Ton/IDU.

## NrsFig
Typical Admin Wing
[11 empty] | Area | L | W | Pct area
[10 empty] | Office | 7500 | 90 | 83.3333 | 53.57%
[10 empty] | Circulation | 2500 | 20 | 125 | 17.86% | Corridor, lobby, lounge, entry
[10 empty] | Facilities | 4000 | 90 | 44.4444 | 28.57% | Mechanical, storage, electrical
14000
[10 empty] | Area/odu | 6500
[10 empty] | Num odu | 2.1538
[10 empty] | Ton/sys | 20
[10 empty] | sf/ton | 325
[10 empty] | Leader | 20
[10 empty] | Header | 100
[10 empty] | Perim Brn | 40
40 | [9 empty] | Core Brn | 20
30
20
10
| 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90
Office
Facilities
Circulation
Office
Facilities
ODU
140 ft
100 ft

## Mtl
Motel | [6 empty] | ODU Capacity
|  |  |  | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | approx sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Brn L | Trg area/unit | Max Ton/IDU | Num IDUs | IDU Config | Goemetry reference | Stories | Vertical
GuestRmUnOcc |  | 12264.32 | 20.45% | 3456 | 72 | 48 | 8 | 8 | 432 | 20 | 60 | 3 | 10 | 10 | 288 | 0.75 | -99 | Ducted | Same as hotel guest room | 2
GuestRm12Occ |  | 25886.38 | 43.16% | 3456 | 72 | 48 | 8 | 8 | 432 | 20 | 60 | 3 | 10 | 10 | 288 | 0.75 | -99 | Ducted | Same as guest room | 2
GuestRm24Occ |  | 12956.38 | 21.6% | 3456 | 72 | 48 | 8 | 8 | 432 | 20 | 60 | 3 | 10 | 10 | 288 | 0.75 | -99 | MIXED | Same as guest room | 2
GuestRmCorrid |  | 6708.04 | 11.19% | 3456 | 72 | 48 | 8 | 8 | 432 | 20 | 60 | 3 | 10 | 10 | 288 | 0.75 | -99 | Ducted | Same as guest room | 2
Laundry |  | 958.72 | 1.599% | 3456 | 72 | 48 | 8 | 8 | 432 | 20 | 60 | 3 | 10 | 10 | 500 | 2 | 1 | Ducted | Same as guest room | 2
OfficeGeneral |  | 1198.52 | 1.998% | 3456 | 72 | 48 | 8 | 8 | 432 | 20 | 60 | 3 | 10 | 10 | 500 | 1.5 | 1 | Surface | Same as guest room | 2
Building Shape
| Len | 277.65 | 55.53 |  | 12 | 23.1375
| Wid | 54 | 10.8
| Area | 14993.1
ODU
278 ft
100 ft
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on S3: Set to -99 to calc in worksheet based on Trg area/unit. Set to "1" to allow DOE2 to calc based on Max Ton/IDU.

## MLI
Light Industrial | [6 empty] | ODU Capacity
|  |  |  | Area/ ODU | Len | Depth | Max ton/sys | Typ ton/sys | approx sf/ton | Ldr | Hdr | Nom Hdr Ht | Perim Brn L | Core Brn L | Trg area/unit | Max Ton/IDU | Num IDUs | IDU Config | Goemetry reference | Stories | Vertical
IndHighBay |  | 80010.1 | 80% | 12000 | 109.5445 | 109.5445 | 36 | 36 | 333.3333 | 20 | 90 | 5 | 30 | 30 | NA | 7 | 1 | Ducted | Similar to auditorium
StorageSmlCond |  | 20004 | 20% | 12000 | 109.5445 | 109.5445 | 36 | 36 | 333.3333 | 20 | 90 | 5 | 30 | 30 | NA | 7 | 1 | Ducted
|  |  |  | appx tons | ton/sys | # sys
| Bldg Area | 100014.1 | 350 | 285.7546 | 36 | 7.9376
| Bldg Len | 316.2501
Note on N3: The nominal elevation change of the header, typically not including floor-to-floor changes.
Note on S3: Set to -99 to calc in worksheet based on Trg area/unit. Set to "1" to allow DOE2 to calc based on Max Ton/IDU.