## DefF
|  |  | New method for TIMED control |  |  |  | New method for ON-DEMAND control
| Existing DOE2 Method |  |  | EPRI Paper
| Timed | Demand |  | Time initiated |  |  |  | Temp init, temp terminated
| existing | existing | accum. | Temp terminated |  |  | accum. | 120 minute period at low dW
dW | DefF | DefF | run time | CapFi | DefF | DefF | run time | CapFi | DefF | DefF
ratio | min | min | min | ratio | min | frac | min | ratio | min | frac
1e-06 | 3.5 | 0.0041491 | 60 | 1 | 1.2 | 0.019608 | 119.9571 | 1 | 0.60021 | 0.0049787
1e-05 | 3.5 | 0.041465 | 60 | 1 | 2.1 | 0.033816 | 119.5714 | 1 | 1.0538 | 0.0087358
6.3e-05 | 3.5 | 0.26028 | 60 | 0.99989 | 2.1006 | 0.033826 | 117.3 | 0.98069 | 1.0745 | 0.009077
0.0001 | 3.5 | 0.41209 | 60 | 0.98808 | 2.1679 | 0.034872 | 115.7143 | 0.95844 | 1.2117 | 0.010363
0.0005 | 3.5 | 2.0053 | 60 | 0.8604 | 2.8957 | 0.04604 | 98.5714 | 0.7578 | 2.1186 | 0.021041
0.001 | 3.5 | 3.881 | 60 | 0.7008 | 3.8054 | 0.059641 | 77.1429 | 0.6096 | 3.3641 | 0.041787
0.0014 | 3.5 | 5.2963 | 60 | 0.57312 | 4.5332 | 0.070246 | 60 | 0.57312 | 4.5332 | 0.070246 | same as for TIMED
Demand should always be |  |  |  | DefF = 7.8 - 5.7 * CapFi |  |  |  | DefF = (7.8 - 5.7 * CapFi) * 60/AccumRunTime
less than or equal to Timed | [6 empty] | Accumulated run time varies with dW due to Temp init
Don't go to zero for demand | [7 empty] | AccumRunTime = 120 - 60 * dW / 0.0014
EPRI tests are described as "timed frost-defrost control set to 45 or 90 minutes"
EPRI defrost length = 7.8 - 5.7 * CapFi
where CapFi is the capacity ratio at the start of the defrost period (instantaneous value)
EPRI dry coil defrost length = 1.1 minutes based on field tests
Comment that "dry coil defrosts are substantially shorter than even lightly frosted coils"
To capture adjustable cycle length for demand defrost:
Accumulated Run Time (frosting mode) =
120 min @ dW = 0
60 min @ dW = 0.0014
AccumRunTime = 120 - 60 * dW / 0.0014
Carrier Demand Defrost Method:
Duration | Cycle period
<3 min | 120
3-5 min | 90
5-7 min | 60
>7 min | 30

## Cap&Pwr
|  | Use for Timed and Demand |  |  |  | Existing DOE2.2 Curves |  |  | Existing DOE2.2 Curves
|  | EPRI Defrost Curves |  |  |  | Timed Defrost |  |  | Demand Defrost
|  | CapF | PwrF | Ratio |  | CapF | PwrF | Ratio |  | CapF | PwrF | Ratio
|  | Q/Qs | P/Ps | P/Q |  | Q/Qs | P/Ps | P/Q | DefF | Q/Qs | P/Ps | P/Q
| C0 | 1.02 | 1 |  | C0 | 0.909 | 0.9
Accum | C1 | -5.32 | -1.8 |  | C1 | -107.33 | -36.45
Runtime | dW | Y = C0 + C1 * dW * t |  |  |  | Y = C0 + C1 * dW |  |  | frac
60 | 1e-06 | 1 | 0.99995 | 0.99995 |  | 0.90889 | 0.89996 | 0.99018 | 6.9152e-05 | 0.87494 | 0.95393 | 1.0903
60 | 0.0001 | 1 | 0.9946 | 0.9946 |  | 0.89827 | 0.89636 | 0.99787 | 0.0068681 | 0.86899 | 0.94745 | 1.0903
60 | 0.0003 | 0.97212 | 0.9838 | 1.012 |  | 0.8768 | 0.88906 | 1.014 | 0.020325 | 0.85722 | 0.93461 | 1.0903
60 | 0.0006 | 0.92424 | 0.9676 | 1.0469 |  | 0.8446 | 0.87813 | 1.0397 | 0.039841 | 0.84014 | 0.91599 | 1.0903
60 | 0.0012 | 0.82848 | 0.9352 | 1.1288 |  | 0.7802 | 0.85626 | 1.0975 | 0.076628 | 0.80795 | 0.8809 | 1.0903
9% power penalty during normal operation at all times!
Use EPRI CapF and PwrF curves for both timed and demand defrost.
Demand will be differentiated from timed via accumulated runtime variable.
See DefF

## VRFCoilUA
Calculation of UA degradation of VRF outdoor unit during defrost with split coil mode
Calculation of surface heat transfer coefficent for a typical heat exchanger
Rows | 3
Laminar air flow | 7.6705 | 1.2159 | 0.625 | mph | Flow ratio
Face velocity | 675 | 107 | 55 | fpm | 0.081481
Fins/inch | 14 | 14 | 14
spacing | 0.0059524 | 0.0059524 | 0.0059524 | feet
Fin thickness | 0.008 | 0.008 | 0.008 | in
fin t/ft | 0.00066667 | 0.00066667 | 0.00066667 | feet
gap | 0.0052857 | 0.0052857 | 0.0052857
Tube spacing | 1.25 | 1.25 | 1.25
Tube dia | 0.375 | 0.375 | 0.375
Gfr | 2956.2044 | 468.6131 | 240.8759 | lbm/hr-sf | at face | 4153.8462
Gc | 5326.4944 | 844.348 | 434.0107 | lbm/hr-sf | in coil
mu | 0.044 | 0.044 | 0.044
Red | 3783.0216 | 599.679 | 308.2462
Rexb | 12610.0719 | 1998.9299 | 1027.4873
j | 0.0072 | 0.012 | 0.012
Cp | 0.24 | 0.24 | 0.24
Pr | 0.71 | 0.71 | 0.71
h | 11.565 | 3.0554 | 1.5706 |  | h = j * Gc * Cp / Pr^2/3
Calculation of surface resistance due to combined natural convection and radiation
typ inside film |  |  | 0.56283 | convect | vertical plate 3 ft tall, DT = 35 |  | ASHRAE 2013 Handbook, Eq T9.14
|  |  | 0.49148 | radiant
total nat conv air film |  |  | 1.0543 | total; slightly below the 55 fpm value from the heat exchanger calcs.
Calculation of UA degradation factor
Example | Normal | Nat conv
UA | 2000 | 2000 | Rated UA value for the outdoor unit from a DOE2.3 VRF simulation
Rtot | 0.0005 | 0.0005 |  |  | R = 1/UA = Rair + Rmedia + Rrefg
Rair | 0.000225 | 0.0024681 | incr inversly to h |  | Rair ~ 1/hair
Rmedia | 0.00015 | 0.00015
Rrefg | 0.000125 | 0.000125
Rtot | 0.0005 | 0.0027431
UA | 2000 | 364.5539
UA Ratio |  | 18.23% | degradation factor for outdoor unit due to operation in natural convection
UAFrost |  | 9.114% | Since only half of heat exchanger is available, decrease by half again