## 2016HVAC Update
DEER2016 Packaged and Split Air Conditioner Update
2015-05-20
IEER Rating Update
The IEER values published in the Technology Definitions for the DEER2015 Update were calculated based on typical expected operation. These values did not always correspond with the rated IEER values published by the equipment manufacturers. For the DEER2016 update, manufacturer rated IEER values were collected and applied to the Technology Definitions.
Impact of fan control on IEER
The type of fan control installed on a system affects the IEER rating. Most manufacturers now provide a description of the fan control that was used in the development of each IEER value. For some units where different fan control options are available, multiple IEER values are listed. In the IEER versus EER data that was collected for the DEER2016 update, the fan control strategy was either constant volume or two-speed. For each unit size range, relationships were established between rated IEER and rated EER for both of these fan control strategies. Both values are now listed in the Measure and Technology tables.
Program Claims
When program claims are made based on IEER ratings, the fan control mode associated with the claimed IEER must be determined and utilized to select the appropriate measure from the DEER database. It is acceptable to interpolate between measures using either EER ratings or appropriate IEER ratings, but extrapolation is not acceptable. The 2016 DEER database is not applicable to 3-speed or variable speed DX systems.
Workbook Contents:
Measure Summary
This worksheet lists all of the packaged and split AC measure IDs that were updated for DEER2016.
Technology Summary
Technology tier levels definitions for commercial split and packaged air conditioners
Measure Definitions
Complete listing of DEER2016 HVAC measure definitions
Technologies
Lists all of the technologies referenced by the updated HVAC measures, including their key parameters.
IEERData_6to11Tons
Development of curves for rated IEER vs. rated EER for 65 to 135 kBtuh units.
IEERData_12to19Tons
Development of curves for rated IEER vs. rated EER for 135 to 240 kBtuh units.
IEERData_20to65Tons
Development of curves for rated IEER vs. rated EER for units 240 kBtuh and larger.

## Measure Summary
Measure Summary
This table lists the DEER2016 measure IDs that are included in this update.
For details on the new measure definitions, see the technology summary worksheets and the "Measure Definitions" worksheet.
EER-rated Packaged Air Conditioners
Measure ID | Measure Tech ID | Rated EER | 1 spd Rated IEER | 2 spd Rated IEER
NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | 11.5 | 12.2 | 14.3
NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | 12 | 12.8 | 14.6
NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | 13 | 13.9 | 15.1
NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | 11.5 | 12.2 | 14.3
NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | 12 | 12.8 | 14.6
NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | 13 | 13.9 | 15.1
NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | dxAC-Com-Pkg-110to135kBTUh-EER11.5 | 11.5 | 12.2 | 14.3
NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | dxAC-Com-Pkg-110to135kBTUh-EER12.0 | 12 | 12.8 | 14.6
NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | dxAC-Com-Pkg-110to135kBTUh-EER12.5 | 12.5 | 13.3 | 14.9
NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | dxAC-Com-Pkg-135to240kBTUh-EER11.5 | 11.5 | 12.4 | 14.2
NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | dxAC-Com-Pkg-135to240kBTUh-EER12.0 | 12 | 13.1 | 14.8
NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | dxAC-Com-Pkg-135to240kBTUh-EER12.5 | 12.5 | 13.8 | 15.5
NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | 10.8 | 11.6 | 12.8
NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | 11.5 | 12.4 | 13.6
NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | 12.5 | 13.6 | 14.8
NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | dxAC-Com-Pkg-gte760kBTUh-EER10.2 | 10.2 | 10.9 | 12.1
NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | dxAC-Com-Pkg-gte760kBTUh-EER11.0 | 11 | 11.8 | 13.1
NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | dxAC-Com-Pkg-gte760kBTUh-EER12.0 | 12 | 13 | 14.2
18

## Technology Summary
DEER2016 Commercial Packaged and Split AC Measure Technology Summary
This table summarizes the key parameters for the DEER2016 commercial packaged and split AC technologies.
HVAC performance map lookups
Associated DEER Measure IDs
Equipment Size Range | Efficiency Tier | Rated EER | Rated IEER (1 spd) | Rated IEER (2 spd) | Supply Fan W/CFM | System Type | Economizer Req'd | Econo in Pre-existing Tech | DEER 2014 Measure ID | DEER2016 Measure ID | ID | EER | W/CFM
65 to 110 kBTU/hr | Code | 11 | 11.6 | 14.1 | 0.4 | 2-speed, single zone | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p0eer NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer |  | 31001 | 11 | 0.4
| 1 | 11.5 | 12.2 | 14.3 | 0.4 | 2-speed, single zone | Yes | No |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | 31101 | 11.5 | 0.4
| 2 | 12 | 12.8 | 14.6 | 0.4 | 2-speed, single zone | Yes | No |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | 31201 | 12 | 0.4
| 3 | 13 | 13.9 | 15.1 | 0.4 | 2-speed, single zone | Yes | No |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | 31301 | 13 | 0.4
| 1 | 11.5 | 12.2 | 14.3 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eerwPreEcono | 31101 | 11.5 | 0.4
| 2 | 12 | 12.8 | 14.6 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eerwPreEcono | 31201 | 12 | 0.4
| 3 | 13 | 13.9 | 15.1 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eerwPreEcono | 31301 | 13 | 0.4
110 to 134 kBTU/hr | Code | 11 | 11.6 | 14.1 | 0.4 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p0eer |  | 32001 | 11 | 0.4
| 1 | 11.5 | 12.2 | 14.3 | 0.4 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | 32101 | 11.5 | 0.4
| 2 | 12 | 12.8 | 14.6 | 0.4 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | 32201 | 12 | 0.4
| 3 | 12.5 | 13.3 | 14.9 | 0.4 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | 32301 | 12.5 | 0.4
135 to 239 kBTU/hr | Code | 10.8 | 11.4 | 13.3 | 0.41 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-135to239kBtuh-10p8eer |  | 33001 | 10.8 | 0.41
| 1 | 11.5 | 12.4 | 14.2 | 0.41 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | 33101 | 11.5 | 0.41
| 2 | 12 | 13.1 | 14.8 | 0.41 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | 33201 | 12 | 0.41
| 3 | 12.5 | 13.8 | 15.5 | 0.41 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | 33301 | 12.5 | 0.41
240 to 759 kBTU/hr | Code | 9.8 | 10.4 | 11.7 | 0.61 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-240to759kBtuh-9p8eer NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p5eer NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer |  | 34002 | 9.8 | 0.61
| 1 | 10.8 | 11.6 | 12.8 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | 34102 | 10.8 | 0.61
| 2 | 11.5 | 12.4 | 13.6 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | 34202 | 11.5 | 0.61
| 3 | 12.5 | 13.6 | 14.8 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | 34302 | 12.5 | 0.61
| Code | 10 | 10.6 | 11.9 | 0.72 | var spd, multi-zone | Yes | Yes |  |  | 34001 | 10 | 0.72
| 1 | 10.8 | 11.6 | 12.8 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | 34101 | 10.8 | 0.72
| 2 | 11.5 | 12.4 | 13.6 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | 34201 | 11.5 | 0.72
| 3 | 12.5 | 13.6 | 14.8 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | 34301 | 12.5 | 0.72
> = 760 kBTU/hr | Code | 9.5 | 10 | 11.3 | 0.61 | 2-speed, single zone | Yes | Yes | NE-HVAC-airAC-SpltPkg-gte760kBtuh-9p5eer NE-HVAC-airAC-SpltPkg-gte760kBtuh-9p7eer NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer |  | 35002 | 9.5 | 0.61
| 1 | 10.2 | 10.9 | 12.1 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | 35102 | 10.2 | 0.61
| 2 | 11 | 11.8 | 13.1 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | 35202 | 11 | 0.61
| 3 | 12 | 13 | 14.2 | 0.61 | 2-speed, single zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | 35302 | 12 | 0.61
| Code | 9.7 | 10.3 | 11.6 | 0.72 | var spd, multi-zone | Yes | Yes |  |  | 35001 | 9.7 | 0.72
| 1 | 10.2 | 10.9 | 12.1 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | 35101 | 10.2 | 0.72
| 2 | 11 | 11.8 | 13.1 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | 35201 | 11 | 0.72
| 3 | 12 | 13 | 14.2 | 0.72 | var spd, multi-zone | Yes | Yes |  | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | 35301 | 12 | 0.72
Notes: | DEER2014 specified a single system type for the two largest size ranges based on the building type without explicitly assigning different BldgHVAC values to the associated energy impacts.
Created by inter-measure weighting the two system types (using IOU-specific weights)
240 to 759 kBTU/hr | 1 | 10.8 | 12.8 |  | wtd | weighted sys type | Yes
| 2 | 11.5 | 13.9 |  | wtd | weighted sys type | Yes
| 3 | 12.5 | 15.6 |  | wtd | weighted sys type | Yes
> = 760 kBTU/hr | 1 | 10.2 | 11.8 |  | wtd | weighted sys type | Yes
| 2 | 11 | 13.1 |  | wtd | weighted sys type | Yes
| 3 | 12 | 14.7 |  | wtd | weighted sys type | Yes
DEER2015 generates energy impacts based on multiple system types if applicable to a given building type and assigns the BldgHVAC types to the associated energy impacts.
Therefore, for DEER2015 the energy impacts associated with measures in the two largest size ranges include impacts for both the packaged single zone (cDXGF) and variable speed multi-zone (cPVVG) sytem types.

## Measure Definitions
DEER Measure Definition
This table formats the DEER2016 measures in the ex ante format.
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | StdCostID | RUL_ID | LegacyID | Qualifier | StartDate | ExpiryDate
Commercial EER-rated packaged AC
801 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
802 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
803 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
804 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
805 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
806 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
807 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | dxAC-Com-Pkg-110to135kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
808 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | dxAC-Com-Pkg-110to135kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
809 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | dxAC-Com-Pkg-110to135kBTUh-EER12.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
810 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | dxAC-Com-Pkg-135to240kBTUh-EER11.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
811 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | dxAC-Com-Pkg-135to240kBTUh-EER12.0 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
812 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | dxAC-Com-Pkg-135to240kBTUh-EER12.5 | Review |  | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
813 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
814 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
815 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
816 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5 | dxAC-Com-Pkg-gte760kBTUh-EER10.2 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
817 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5 | dxAC-Com-Pkg-gte760kBTUh-EER11.0 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01
818 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-02 12:00 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | [7 empty] | f | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER |  | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5 | dxAC-Com-Pkg-gte760kBTUh-EER12.0 | Review | Std and Meas Technologies vary by system configuration | f | f |  | ErRobNc |  | HVAC-airAC |  | None | 2015-01-01

## Technologies
DEER2016 HVAC Technology Definitions
This table defines the key equipment parameters for all technologies referenced by the updated measures.
| EER-Rated Pkg AC |  |  |  |  | 5 |  |  |  | 8 | 9 | 10 | 11
UnitID | EER-rated packaged Air Conditioner | Version | Case | 1spd-IEER | 2spd-IEER | EER | Min_CoolCap | Max_CoolCap | CondType | SensCapRatio | COOLING-EIR | CFMperTon | WperCFM | CrankRatio | CRANKCASE-MAX-T | Economizer | Fan_spd | BldgHVAC | PerfCurveID | Technology Description | Pre-existing technology Description (lookup is based on Code ID)
31001 | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | DEER2015 | Code/Standard | 11.6 | 14.1 | 11 | 65 | 110 | Air | 0.663 | 0.27299 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo |  | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo
31101 | dxAC-Com-Pkg-65to110kBTUh-EER11.5 | DEER2015 | Measure | 12.2 | 14.3 | 11.5 | 65 | 110 | Air | 0.663 | 0.25964 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo
31201 | dxAC-Com-Pkg-65to110kBTUh-EER12.0 | DEER2015 | Measure | 12.8 | 14.6 | 12 | 65 | 110 | Air | 0.663 | 0.24716 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo
31301 | dxAC-Com-Pkg-65to110kBTUh-EER13.0 | DEER2015 | Measure | 13.9 | 15.1 | 13 | 65 | 110 | Air | 0.663 | 0.22552 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo
32001 | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | DEER2015 | Code/Standard | 11.6 | 14.1 | 11 | 110 | 135 | Air | 0.663 | 0.27299 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo
32101 | dxAC-Com-Pkg-110to135kBTUh-EER11.5 | DEER2015 | Measure | 12.2 | 14.3 | 11.5 | 110 | 135 | Air | 0.663 | 0.25964 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo
32201 | dxAC-Com-Pkg-110to135kBTUh-EER12.0 | DEER2015 | Measure | 12.8 | 14.6 | 12 | 110 | 135 | Air | 0.663 | 0.24716 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo
32301 | dxAC-Com-Pkg-110to135kBTUh-EER12.5 | DEER2015 | Measure | 13.3 | 14.9 | 12.5 | 110 | 135 | Air | 0.663 | 0.23591 | 318 | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo
33001 | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | DEER2015 | Code/Standard | 11.4 | 13.3 | 10.8 | 135 | 240 | Air | 0.696 | 0.27372 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo
33101 | dxAC-Com-Pkg-135to240kBTUh-EER11.5 | DEER2015 | Measure | 12.4 | 14.2 | 11.5 | 135 | 240 | Air | 0.696 | 0.25481 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo
33201 | dxAC-Com-Pkg-135to240kBTUh-EER12.0 | DEER2015 | Measure | 13.1 | 14.8 | 12 | 135 | 240 | Air | 0.696 | 0.24278 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo
33301 | dxAC-Com-Pkg-135to240kBTUh-EER12.5 | DEER2015 | Measure | 13.8 | 15.5 | 12.5 | 135 | 240 | Air | 0.696 | 0.23149 | 326.4 | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo
34002 | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | DEER2015 | Code/Standard | 10.4 | 11.7 | 9.8 | 240 | 760 | Air | 0.705 | 0.28622 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), two-speed fan, w/Econo
34102 | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | DEER2015 | Measure | 11.6 | 12.8 | 10.8 | 240 | 760 | Air | 0.705 | 0.25464 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo
34202 | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | DEER2015 | Measure | 12.4 | 13.6 | 11.5 | 240 | 760 | Air | 0.705 | 0.23585 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo
34302 | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | DEER2015 | Measure | 13.6 | 14.8 | 12.5 | 240 | 760 | Air | 0.705 | 0.21257 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo
34001 | dxAC-Com-Pkg-240to760kBTUh-EER10.0 | DEER2015 | Code/Standard | 10.6 | 11.9 | 10 | 240 | 760 | Air | 0.708 | 0.28182 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10 (1 spd IEER = 10.6, 2 spd IEER = 11.9), EIR = 0.282, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), var-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), var-speed fan, w/Econo; 2010 - 2013: EER = 10 (1 spd IEER = 11.9, 2 spd IEER = 11.9), var-speed fan, w/Econo; 2014 - 2015: EER = 10 (1 spd IEER = 11.9, 2 spd IEER = 11.9), var-speed fan, w/Econo
34101 | dxAC-Com-Pkg-240to760kBTUh-EER10.8 | DEER2015 | Measure | 11.6 | 12.8 | 10.8 | 240 | 760 | Air | 0.708 | 0.25619 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.256, Fan W/CFM = 0.72, var-speed fan, with Econo
34201 | dxAC-Com-Pkg-240to760kBTUh-EER11.5 | DEER2015 | Measure | 12.4 | 13.6 | 11.5 | 240 | 760 | Air | 0.708 | 0.23663 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.237, Fan W/CFM = 0.72, var-speed fan, with Econo
34301 | dxAC-Com-Pkg-240to760kBTUh-EER12.5 | DEER2015 | Measure | 13.6 | 14.8 | 12.5 | 240 | 760 | Air | 0.708 | 0.21235 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.212, Fan W/CFM = 0.72, var-speed fan, with Econo
35002 | dxAC-Com-Pkg-gte760kBTUh-EER9.5 | DEER2015 | Code/Standard | 10 | 11.3 | 9.5 | 760 |  | Air | 0.705 | 0.29707 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), two-speed fan, w/Econo
35102 | dxAC-Com-Pkg-gte760kBTUh-EER10.2 | DEER2015 | Measure | 10.9 | 12.1 | 10.2 | 760 |  | Air | 0.705 | 0.27298 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo
35202 | dxAC-Com-Pkg-gte760kBTUh-EER11.0 | DEER2015 | Measure | 11.8 | 13.1 | 11 | 760 |  | Air | 0.705 | 0.24907 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo
35302 | dxAC-Com-Pkg-gte760kBTUh-EER12.0 | DEER2015 | Measure | 13 | 14.2 | 12 | 760 |  | Air | 0.705 | 0.22373 | 320.4 | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo
35001 | dxAC-Com-Pkg-gte760kBTUh-EER9.7 | DEER2015 | Code/Standard | 10.3 | 11.6 | 9.7 | 760 |  | Air | 0.708 | 0.29277 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7 (1 spd IEER = 10.3, 2 spd IEER = 11.6), EIR = 0.293, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), var-speed fan, w/Econo; 2006 - 2009: EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), var-speed fan, w/Econo; 2010 - 2013: EER = 9.7 (1 spd IEER = 11.6, 2 spd IEER = 11.6), var-speed fan, w/Econo; 2014 - 2015: EER = 9.7 (1 spd IEER = 11.6, 2 spd IEER = 11.6), var-speed fan, w/Econo
35101 | dxAC-Com-Pkg-gte760kBTUh-EER10.2 | DEER2015 | Measure | 10.9 | 12.1 | 10.2 | 760 |  | Air | 0.708 | 0.27513 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.275, Fan W/CFM = 0.72, var-speed fan, with Econo
35201 | dxAC-Com-Pkg-gte760kBTUh-EER11.0 | DEER2015 | Measure | 11.8 | 13.1 | 11 | 760 |  | Air | 0.708 | 0.25044 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.25, Fan W/CFM = 0.72, var-speed fan, with Econo
35301 | dxAC-Com-Pkg-gte760kBTUh-EER12.0 | DEER2015 | Measure | 13 | 14.2 | 12 | 760 |  | Air | 0.708 | 0.22398 | 321.6 | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.72, var-speed fan, with Econo
7900473 | dxAC-Com-Pkg-65to110kBTUh-EER10.1 | DEER2015 | Pre-2005 | 10.6 | 13.6 | 10.1 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | FALSE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), EIR = 0, Fan W/CFM = 0.4, one-speed fan, without Econo | EER-Rated Pkg AC, 65-110 kBTU/h | Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo | Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo
7900573 | dxAC-Com-Pkg-65to110kBTUh-EER10.1 | DEER2015 | 2006 - 2009 | 10.6 | 13.6 | 10.1 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | FALSE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), EIR = 0, Fan W/CFM = 0.4, one-speed fan, without Econo |  | 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo | 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo
7900673 | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | DEER2015 | 2010 - 2013 | 11.6 | 14.1 | 11 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | FALSE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0, Fan W/CFM = 0.4, one-speed fan, without Econo |  | 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo | 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo
7900773 | dxAC-Com-Pkg-65to110kBTUh-EER11.0 | DEER2015 | 2014 - 2015 | 11.6 | 14.1 | 11 | 65 | 110 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0, Fan W/CFM = 0.4, two-speed fan, with Econo |  | 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo
13600473 | dxAC-Com-Pkg-110to135kBTUh-EER10.1 | DEER2015 | Pre-2005 | 10.6 | 13.6 | 10.1 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), EIR = 0, Fan W/CFM = 0.4, one-speed fan, with Econo | EER-Rated Pkg AC, 110-135 kBTU/h | Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo | Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo
13600573 | dxAC-Com-Pkg-110to135kBTUh-EER10.1 | DEER2015 | 2006 - 2009 | 10.6 | 13.6 | 10.1 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), EIR = 0, Fan W/CFM = 0.4, one-speed fan, with Econo |  | 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo
13600673 | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | DEER2015 | 2010 - 2013 | 11.6 | 14.1 | 11 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0, Fan W/CFM = 0.4, one-speed fan, with Econo |  | 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo
13600773 | dxAC-Com-Pkg-110to135kBTUh-EER11.0 | DEER2015 | 2014 - 2015 | 11.6 | 14.1 | 11 | 110 | 135 | Air |  |  |  | 0.4 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0, Fan W/CFM = 0.4, two-speed fan, with Econo |  | 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo
13900473 | dxAC-Com-Pkg-135to240kBTUh-EER9.5 | DEER2015 | Pre-2005 | 11.4 | 11.6 | 9.5 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), EIR = 0, Fan W/CFM = 0.41, one-speed fan, with Econo | EER-Rated Pkg AC, 135-240 kBTU/h | Pre-2005: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo
13900573 | dxAC-Com-Pkg-135to240kBTUh-EER9.5 | DEER2015 | 2006 - 2009 | 11.4 | 11.6 | 9.5 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), EIR = 0, Fan W/CFM = 0.41, one-speed fan, with Econo |  | 2006 - 2009: EER = 9.5 (1 spd IEER = 11.4, 2 spd IEER = 11.6), one-speed fan, w/Econo
13900673 | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | DEER2015 | 2010 - 2013 | 11.4 | 13.3 | 10.8 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0, Fan W/CFM = 0.41, one-speed fan, with Econo |  | 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo
13900773 | dxAC-Com-Pkg-135to240kBTUh-EER10.8 | DEER2015 | 2014 - 2015 | 11.4 | 13.3 | 10.8 | 135 | 240 | Air |  |  |  | 0.41 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0, Fan W/CFM = 0.41, two-speed fan, with Econo |  | 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo
10400473 | dxAC-Com-Pkg-240to760kBTUh-EER9.3 | DEER2015 | Pre-2005 | 11.1 | 11.1 | 9.3 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo | EER-Rated Pkg AC, 240-760 kBTU/h | Pre-2005: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo
10400573 | dxAC-Com-Pkg-240to760kBTUh-EER9.3 | DEER2015 | 2006 - 2009 | 11.1 | 11.1 | 9.3 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  | 2006 - 2009: EER = 9.3 (1 spd IEER = 11.1, 2 spd IEER = 11.1), one-speed fan, w/Econo
10400673 | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | DEER2015 | 2010 - 2013 | 11.7 | 11.7 | 9.8 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  | 2010 - 2013: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), one-speed fan, w/Econo
10400773 | dxAC-Com-Pkg-240to760kBTUh-EER9.8 | DEER2015 | 2014 - 2015 | 11.7 | 11.7 | 9.8 | 240 | 760 | Air |  |  |  | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), EIR = 0, Fan W/CFM = 0.61, two-speed fan, with Econo |  | 2014 - 2015: EER = 9.8 (1 spd IEER = 11.7, 2 spd IEER = 11.7), two-speed fan, w/Econo
10400460 | dxAC-Com-Pkg-240to760kBTUh-EER9.5 | DEER2015 | Pre-2005 | 11.3 | 11.3 | 9.5 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-Rated Pkg AC, 240-760 kBTU/h | Pre-2005: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), var-speed fan, w/Econo
10400560 | dxAC-Com-Pkg-240to760kBTUh-EER9.5 | DEER2015 | 2006 - 2009 | 11.3 | 11.3 | 9.5 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  | 2006 - 2009: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), var-speed fan, w/Econo
10400660 | dxAC-Com-Pkg-240to760kBTUh-EER10.0 | DEER2015 | 2010 - 2013 | 11.9 | 11.9 | 10 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10 (1 spd IEER = 11.9, 2 spd IEER = 11.9), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  | 2010 - 2013: EER = 10 (1 spd IEER = 11.9, 2 spd IEER = 11.9), var-speed fan, w/Econo
10400760 | dxAC-Com-Pkg-240to760kBTUh-EER10.0 | DEER2015 | 2014 - 2015 | 11.9 | 11.9 | 10 | 240 | 760 | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10 (1 spd IEER = 11.9, 2 spd IEER = 11.9), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  | 2014 - 2015: EER = 10 (1 spd IEER = 11.9, 2 spd IEER = 11.9), var-speed fan, w/Econo
10500473 | dxAC-Com-Pkg-gte760kBTUh-EER9.0 | DEER2015 | Pre-2005 | 10.7 | 10.7 | 9 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo | EER-Rated Pkg AC, 760+ kBTU/h | Pre-2005: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo
10500573 | dxAC-Com-Pkg-gte760kBTUh-EER9.0 | DEER2015 | 2006 - 2009 | 10.7 | 10.7 | 9 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  | 2006 - 2009: EER = 9 (1 spd IEER = 10.7, 2 spd IEER = 10.7), one-speed fan, w/Econo
10500673 | dxAC-Com-Pkg-gte760kBTUh-EER9.5 | DEER2015 | 2010 - 2013 | 11.3 | 11.3 | 9.5 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | one-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), EIR = 0, Fan W/CFM = 0.61, one-speed fan, with Econo |  | 2010 - 2013: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), one-speed fan, w/Econo
10500773 | dxAC-Com-Pkg-gte760kBTUh-EER9.5 | DEER2015 | 2014 - 2015 | 11.3 | 11.3 | 9.5 | 760 |  | Air |  |  |  | 0.61 | 0 | 100 | TRUE | two-speed | cDXGF |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), EIR = 0, Fan W/CFM = 0.61, two-speed fan, with Econo |  | 2014 - 2015: EER = 9.5 (1 spd IEER = 11.3, 2 spd IEER = 11.3), two-speed fan, w/Econo
10500460 | dxAC-Com-Pkg-gte760kBTUh-EER9.2 | DEER2015 | Pre-2005 | 11 | 11 | 9.2 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo | EER-Rated Pkg AC, 760+ kBTU/h | Pre-2005: EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), var-speed fan, w/Econo
10500560 | dxAC-Com-Pkg-gte760kBTUh-EER9.2 | DEER2015 | 2006 - 2009 | 11 | 11 | 9.2 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  | 2006 - 2009: EER = 9.2 (1 spd IEER = 11, 2 spd IEER = 11), var-speed fan, w/Econo
10500660 | dxAC-Com-Pkg-gte760kBTUh-EER9.7 | DEER2015 | 2010 - 2013 | 11.6 | 11.6 | 9.7 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7 (1 spd IEER = 11.6, 2 spd IEER = 11.6), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  | 2010 - 2013: EER = 9.7 (1 spd IEER = 11.6, 2 spd IEER = 11.6), var-speed fan, w/Econo
10500760 | dxAC-Com-Pkg-gte760kBTUh-EER9.7 | DEER2015 | 2014 - 2015 | 11.6 | 11.6 | 9.7 | 760 |  | Air |  |  |  | 0.72 | 0 | 100 | TRUE | var-speed | cPVVT |  | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.7 (1 spd IEER = 11.6, 2 spd IEER = 11.6), EIR = 0, Fan W/CFM = 0.72, var-speed fan, with Econo |  | 2014 - 2015: EER = 9.7 (1 spd IEER = 11.6, 2 spd IEER = 11.6), var-speed fan, w/Econo

## IEERData_6to11Tons
65 to 135 kBtuh
Rated IEER
Mfgr | Nom Cap | Model # | Heat Source | Rated EER | 1 Spd Fan | 2 Spd Fan
McQuay | 12 | MPS 012B (R410A) | Gas/Elec | 11 | 10.8 | 13.5
York | 7.5 | ZXG08 (R410A) | Gas | 11 | 11.5 | n/a
York | 7.5 | ZXE08 (R410A) | Elec | 11.2 | 11.6 | n/a
York | 10 | ZYG12 (R410A) | Gas | 11.5 | 11.6 | 14.4
York | 8.5 | ZXG09 (R410A) | Gas | 11 | 11.7 | n/a
McQuay | 6 | MPS 006B (R410A) | Gas/Elec | 11.3 | 11.8 | n/a
Ruud | 6 | RLNL-C073 (R410A) | Elec | 11.2 | 11.8 | n/a
Ruud | 6 | RKNL-C073 (R410A) | Gas | 11 | 11.8 | n/a
Lennox | 7.5 | KGA092S4M | Gas | 11 | 11.8 | 13
Lennox | 8.5 | KGA102S4M | Gas | 11 | 11.8 | 13
Lennox | 10 | KGA120S4M | Elec | 11 | 11.8 | 13
York | 10 | ZXG12 (R410A) | Gas | 11 | 11.8 | 14.4
York | 6 | ZXG07 (R410A) | Gas | 11 | 11.9 | n/a
McQuay | 7 | MPS 007B (R410A) | Gas/Elec | 11.2 | 11.9 | 14.5
Ruud | 7.5 | RKNL-C090 (R410A) | Elec | 11.2 | 11.9 | 14.5
York | 8.5 | ZXE09 (R410A) | Elec | 11.2 | 11.9 | n/a
McQuay | 10 | MPS 010B (R410A) | Gas/Elec | 11.2 | 11.9 | 14.6
Ruud | 10 | RKNL-C120 (R410A) | Gas | 11.2 | 11.9 | 14.4
McQuay | 8 | MPS 008B (R410A) | Gas/Elec | 11.2 | 12 | 14.4
Ruud | 8.5 | RKNL-C102 (R410A) | Gas | 11.2 | 12 | 14.4
York | 10 | ZXE12 (R410A) | Elec | 11.2 | 12 | 14.8
York | 6 | ZXE07 (R410A) | Elec | 11.2 | 12.1 | n/a
Ruud | 7.5 | RKKL-B090 (R410A) | Gas | 11.2 | 12.1 | n/a
Ruud | 10 | RKKL-B120 (R410A) | Gas | 11.2 | 12.2 | n/a
York | 7.5 | ZYG08 (R410A) | Gas | 12 | 12.4 | n/a
York | 8.5 | ZYG09 (R410A) | Gas | 12 | 12.4 | n/a
York | 6 | ZYG07 (R410A) | Gas | 12 | 12.6 | n/a
York | 8.5 | ZYE09 (R410A) | Elec | 12.2 | 12.6 | n/a
York | 6 | ZYE07 (R410A) | Elec | 12.2 | 12.8 | n/a
Lennox | 8.5 | KGA102H4M | Gas | 12.2 | 12.9 | 14
Carrier | 6 | 50PG07 (R410A) | Elec | 12.2 | 13 | n/a
Carrier | 6 | 48PG07 (R410A) | Gas | 12 | 13 | n/a
Lennox | 7.5 | KGA092H4M | Gas | 12.5 | 13 | 14
Carrier | 10 | 48PG12 (R410A) | Gas | 12 | 13 | n/a
Lennox | 10 | KGA120H4M | Gas | 12 | 13 | 13.8
Carrier | 8.5 | 50PG09 (R410A) | Elec | 12.4 | 13.4 | n/a
Carrier | 8.5 | 48PG09 (R410A) | Gas | 12.2 | 13.4 | n/a
Carrier | 7.5 | 50PG08 (R410A) | Elec | 12.7 | 13.5 | n/a
Carrier | 7.5 | 48PG08 (R410A) | Gas | 12.5 | 13.5 | n/a
Ruud | 10 | RLRL-C120 (R410A) | Gas | 12.5 | 13.8 | 15.6
Ruud | 7.5 | RLRL-C090 (R410A) | Elec | 13 | 14 | 15.8
York | 10 | ZYE12 (R410A) | Elec | 11.7 | 11.8 | 14.4
Mfgr | Nom Cap | Model # | Heat Source | Rated EER | 1 Spd Fan | 2 Spd Fan
Lennox | 7.5 | KGA092S4M | Gas | 11 | 11.8 | 13
McQuay | 12 | MPS 012B (R410A) | Gas/Elec | 11 | 10.8 | 13.5
Lennox | 10 | KGA120H4M | Gas | 12 | 13 | 13.8
Lennox | 7.5 | KGA092H4M | Gas | 12.5 | 13 | 14
Lennox | 8.5 | KGA102H4M | Gas | 12.2 | 12.9 | 14
McQuay | 8 | MPS 008B (R410A) | Gas/Elec | 11.2 | 12 | 14.4
Ruud | 8.5 | RKNL-C102 (R410A) | Gas | 11.2 | 12 | 14.4
Ruud | 10 | RKNL-C120 (R410A) | Gas | 11.2 | 11.9 | 14.4
York | 10 | ZXG12 (R410A) | Gas | 11 | 11.8 | 14.4
York | 10 | ZYG12 (R410A) | Gas | 11.5 | 11.6 | 14.4
York | 10 | ZYE12 (R410A) | Elec | 11.7 | 11,8 | 14.4
McQuay | 7 | MPS 007B (R410A) | Gas/Elec | 11.2 | 11.9 | 14.5
Ruud | 7.5 | RKNL-C090 (R410A) | Elec | 11.2 | 11.9 | 14.5
McQuay | 10 | MPS 010B (R410A) | Gas/Elec | 11.2 | 11.9 | 14.6
York | 10 | ZXE12 (R410A) | Elec | 11.2 | 12 | 14.8
Ruud | 10 | RLRL-C120 (R410A) | Gas | 12.5 | 13.8 | 15.6
Ruud | 7.5 | RLRL-C090 (R410A) | Elec | 13 | 14 | 15.8
Carrier | 6 | 50PG07 (R410A) | Elec | 12.2 | 13 | n/a
Carrier | 6 | 48PG07 (R410A) | Gas | 12 | 13 | n/a
McQuay | 6 | MPS 006B (R410A) | Gas/Elec | 11.3 | 11.8 | n/a
Ruud | 6 | RLNL-C073 (R410A) | Elec | 11.2 | 11.8 | n/a
Ruud | 6 | RKNL-C073 (R410A) | Gas | 11 | 11.8 | n/a
Ruud | 6 | RKKL-B072 (R410A) | Gas | 11.2 | n/a | n/a
York | 6 | ZXG07 (R410A) | Gas | 11 | 11.9 | n/a
York | 6 | ZXE07 (R410A) | Elec | 11.2 | 12.1 | n/a
York | 6 | ZYG07 (R410A) | Gas | 12 | 12.6 | n/a
York | 6 | ZYE07 (R410A) | Elec | 12.2 | 12.8 | n/a
Carrier | 7.5 | 50GJ08 (R407C) | Elec | 10.1 | n/a | n/a
Carrier | 7.5 | 48GJ08 (R407C) | Gas | 10.1 | n/a | n/a
Carrier | 7.5 | 50PG08 (R410A) | Elec | 12.7 | 13.5 | n/a
Carrier | 7.5 | 48PG08 (R410A) | Gas | 12.5 | 13.5 | n/a
Ruud | 7.5 | RKKL-B090 (R410A) | Gas | 11.2 | 12.1 | n/a
Ruud | 7.5 | RLNL-B090 (R410A) | Elec | 11.2 | 11.9 | n/a
York | 7.5 | ZXG08 (R410A) | Gas | 11 | 11.5 | n/a
York | 7.5 | ZXE08 (R410A) | Elec | 11.2 | 11.6 | n/a
York | 7.5 | ZYG08 (R410A) | Gas | 12 | 12.4 | n/a
York | 7.5 | ZYE08 (R410A) | Elec | 12.2 | 12.6 | n/a
Carrier | 8.5 | 50PG09 (R410A) | Elec | 12.4 | 13.4 | n/a
Carrier | 8.5 | 48PG09 (R410A) | Gas | 12.2 | 13.4 | n/a
Ruud | 8.5 | RLNL-B102 (R410A) | Elec | 11.2 | 12 | n/a
York | 8.5 | ZXG09 (R410A) | Gas | 11 | 11.7 | n/a
York | 8.5 | ZXE09 (R410A) | Elec | 11.2 | 11.9 | n/a
York | 8.5 | ZYG09 (R410A) | Gas | 12 | 12.4 | n/a
York | 8.5 | ZYE09 (R410A) | Elec | 12.2 | 12.6 | n/a
Carrier | 10 | 50GJ120 (R407C) | Elec | 10.1 | n/a | n/a
Carrier | 10 | 48GJ120 (R407C) | Gas | 10.1 | n/a | n/a
Carrier | 10 | 50PG12 (R410A) | Elec | 12 | 13 | n/a
Carrier | 10 | 48PG12 (R410A) | Gas | 12 | 13 | n/a
Ruud | 10 | RKKL-B120 (R410A) | Gas | 11.2 | 12.2 | n/a
Ruud | 10 | RLNL-B120 (R410A) | Elec | 11.2 | 11.9 | n/a

## IEERData_12to19Tons
135 to 240 kBtuh
Rated IEER
Mfgr | Nom Cap | Model # | Heat Source | Rated EER | 1 Spd Fan | 2 Spd Fan
McQuay | 12 | MPS 012B (R410A) | Gas/Elec | 11 | 10.8 | 13.5
Ruud | 20 | RKKL-B240 (R410A) | Gas | 10.5 | 10.5 | n/a
Ruud | 12.5 | RKKL-C151 (R410A) | Gas | 11.1 | 10.8 | n/a
York | 20 | ZF240N (R410A) | Gas | 10 | 10.8 | n/a
Lennox | 15 | KGA180S4M | Gas | 10.8 | 11 | 12.8
Lennox | 20 | KGA240S4M | Gas | 10.8 | 11 | 13
Ruud | 15 | RKKL-B180 (R410A) | Gas | 10.9 | 11.1 | n/a
Ruud | 15 | RLKL-B180 (R410A) | Elec | 11 | 11.1 | n/a
Lennox | 12.5 | KGA150S4M | Gas | 11 | 11.4 | 12
Carrier | 20 | 48A2-020 | Gas | 10.1 | 11.4 | n/a
McQuay | 20 | MPS 020B (R410A) | Gas/Elec | 11.1 | 11.4 | 14.8
Ruud | 20 | RKNL-C240 (R410A) | Gas | 11.1 | 11.4 | 14.8
Carrier | 12.5 | 48PG14 (R410A) | Gas | 11.4 | 11.6 | n/a
Carrier | 12.5 | 50PG14 (R410A) | Elec | 11.5 | 11.6 | n/a
Carrier | 20 | 50A2-020 | Elec | 10.3 | 11.7 | 11.8
York | 17.5 | ZF210N (R410A) | Gas | 11 | 11.9 | n/a
Lennox | 17.5 | KGA210S4M | Gas | 10.8 | 12 | 13.1
York | 15 | ZF180N (R410A) | Gas | 11 | 12.1 | n/a
McQuay | 15 | MPS 015B (R410A) | Gas/Elec | 11.1 | 12.4 | 14.6
Ruud | 15 | RKNL-C180 (R410A) | Gas | 11.1 | 12.4 | 14.4
Ruud | 17.5 | RKNL-C210 (R410A) | Gas | 11.6 | 12.6 | 14.5
Lennox | 17.5 | KGA210H4M | Gas | 12 | 13 | 14
York | 20 | ZJ240N (R410A) | Gas | 11.5 | 13 | n/a
Lennox | 20 | KGA240H4M | Gas | 12 | 13.2 | 14.5
York | 17.5 | ZJ210N (R410A) | Gas | 12 | 13.4 | n/a
Lennox | 15 | KGA180H4M | Gas | 12 | 13.5 | 13.7
Lennox | 13 | KGA156H4M | Gas | 12 | 13.6 | 14.1
York | 15 | ZJ180N (R410A) | Gas | 12.4 | 14 | n/a
Lennox | 20 | SGC240H4M | Gas | 12.6 | 14.2 | 16.6
Mfgr | Nom Cap | Model # | Heat Source | Rated EER | 1 Spd Fan | 2 Spd Fan
Carrier | 20 | 50A2-020 | Elec | 10.3 | 11.7 | 11.8
Lennox | 12.5 | KGA150S4M | Gas | 11 | 11.4 | 12
Lennox | 15 | KGA180S4M | Gas | 10.8 | 11 | 12.8
Lennox | 20 | KGA240S4M | Gas | 10.8 | 11 | 13
Lennox | 17.5 | KGA210S4M | Gas | 10.8 | 12 | 13.1
McQuay | 12 | MPS 012B (R410A) | Gas/Elec | 11 | 10.8 | 13.5
Lennox | 15 | KGA180H4M | Gas | 12 | 13.5 | 13.7
Lennox | 17.5 | KGA210H4M | Gas | 12 | 13 | 14
Lennox | 13 | KGA156H4M | Gas | 12 | 13.6 | 14.1
Ruud | 15 | RKNL-C180 (R410A) | Gas | 11.1 | 12.4 | 14.4
Ruud | 17.5 | RKNL-C210 (R410A) | Gas | 11.6 | 12.6 | 14.5
Lennox | 20 | KGA240H4M | Gas | 12 | 13.2 | 14.5
McQuay | 15 | MPS 015B (R410A) | Gas/Elec | 11.1 | 12.4 | 14.6
Ruud | 15 | RLNL-C180 (R410A) | Elec | 11.1 | 12.4 | 14.6
McQuay | 20 | MPS 020B (R410A) | Gas/Elec | 11.1 | 11.4 | 14.8
Ruud | 20 | RKNL-C240 (R410A) | Gas | 11.1 | 11.4 | 14.8
Lennox | 20 | SGC240H4M | Gas | 12.6 | 14.2 | 16.6

## IEERData_20to65Tons
240 to 760 kBtuh
Rated IEER
Mfgr | Nom Cap | Model # | Heat Source | Rated EER | 1 Spd Fan
Carrier | 60 | 50A2-060 | Elec | 10.2 | 11.4
York | 30 | Z33+C0(2,4,5) | Gas | 10.1 | 11.1
Carrier | 60 | 48A2-060 | Gas | 10.1 | 11.1
Carrier | 40 | 48A2-040 | Gas | 10.3 | 11
York | 40 | Z34+C0(2,4,5) | Gas | 10 | 10.5
Lennox | 45 | LGH540S4 | Gas | 10 | 10.5
Lennox | 50 | LGH600S4V | Gas | 9.8 | 10.3
Lennox | 50 | LCH600S4V | Elec | 10 | 10.3
Lennox | 40 | LGH480S4V | Gas | 9.8 | 10.1
Lennox | 35 | LGH420S4V | Gas | 10 | 10.2
Carrier | 40 | 50A2-040 | Elec | 10.5 | 11.2
York | 25 | Z42+C0(2,4,5) | Gas | 10.5 | 11.5
Lennox | 30 | LGH360H4V | Gas | 10.6 | 11.5
Lennox | 35 | LGH420H4V | Gas | 10.8 | 11.3
Lennox | 30 | LCH360H4V | Elec | 10.8 | 11.5
Lennox | 40 | LGH480H4V | Gas | 10.8 | 12
Lennox | 25 | LGH300H4V | Gas | 11.6 | 12.5
Lennox | 25 | LCH300H4V | Elec | 11.8 | 12.5
Mfgr | Nom Cap | Model # | Heat Source | Rated EER |  | 2 Spd Fan
Lennox | 35 | LGH420S4V | Gas | 10 |  | 11
Lennox | 40 | LGH480S4V | Gas | 9.8 |  | 11
Lennox | 40 | LCH480S4V | Elec | 10 |  | 11
Lennox | 50 | LGH600S4V | Gas | 9.8 |  | 11
Lennox | 50 | LCH600S4V | Elec | 10 |  | 11
Lennox | 45 | LGH540S4 | Gas | 10 |  | 11.7
Carrier | 30 | 50A2-030 | Elec | 10.1 |  | 12.4
Carrier | 25 | 50A2-025 | Elec | 10.1 |  | 12.5
Carrier | 27 | 50A2-027 | Elec | 10.2 |  | 12.5
Lennox | 35 | LGH420H4V | Gas | 10.8 |  | 12.5
Lennox | 35 | LCH420H4V | Elec | 10.8 |  | 12.5
Lennox | 40 | LGH480H4V | Gas | 10.8 |  | 13
Lennox | 40 | LCH480H4V | Elec | 10.8 |  | 13
Carrier | 40 | 50A2-040 | Elec | 10.5 |  | 13.1
Carrier | 60 | 50A2-060 | Elec | 10.2 |  | 13.1
Carrier | 35 | 50A2-035 | Elec | 10.1 |  | 13.2
Lennox | 30 | LGH360H4V | Gas | 10.6 |  | 13.5
Lennox | 30 | LCH360H4V | Elec | 10.8 |  | 13.5
Lennox | 25 | LGH300H4V | Gas | 11.6 |  | 14.3
Carrier | 35 | 50A2-035 | Elec | 10.1 |  | 12.4
Carrier | 25 | 50A2-025 | Elec | 10.1 |  | 12.3
Carrier | 27 | 50A2-027 | Elec | 10.2 |  | 12.3
York | 50 | YPAL050N | Gas | 10 |  | 12.17
Carrier | 25 | 48A2-025 | Gas | 10 |  | 12
York | 50 | YPAL050E | Elec | 10.3 |  | 12.17
York | 60 | YPAL060N | Gas | 9.8 |  | 11.83
Carrier | 27 | 48A2-027 | Gas | 10.1 |  | 12
Carrier | 30 | 50A2-030 | Elec | 10.1 |  | 11.9
Carrier | 35 | 48A2-035 | Gas | 10 |  | 11.8
York | 60 | YPAL060E | Elec | 10.1 |  | 11.83
Carrier | 30 | 48A2-030 | Gas | 10 |  | 11.7
York | 55 | YPAL051N | Gas | 9.9 |  | 11.56
York | 55 | YPAL051E | Elec | 10.2 |  | 11.56
Lennox | 25 | LCH300H4V | Elec | 11.8 |  | 12.5