## Equation sources
| Equation | Source
EER to COP | COP = EER / 3.41214 | definitions of COP and EER
COP to EIR | EIR = 1 / COP | definitions of COP and EIR
Note these equations are appropriate for single-speed units only
SEER to EER if SEER <= 26 | EER = −0.02 × SEER² + 1.12 × SEER | Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder (cited in Building America House Simulation Protocols)
else | EER = 15.6 | Dominion TRM 2023, DNV
HSPF to COP if HSPF <=11.7 | COP = −0.0255 × HSPF² + 0.6239 × HSPF | Wassmer, M. (2003). A Component-Based Model for Residential Air Conditioner and Heat Pump Energy Calculations. Masters Thesis, University of Colorado at Boulder
else | COP = HSPF/3.412 | Dominion TRM 2023, DNV
SEER to SEER2 AC system | SEER2 = 0.974 (SEER) - 0.16 | Solaris Technical, LLC. 2022. "Crosswalk Methods for HVAC Efficiency Test Ratings via Appendix M to Appendix M1." Prepared for San Diego Gas and Electric (SDG&E) & Southern California Edison (SCE). November 2.
SEER2 to SEER AC system | SEER = 1.0267 (SEER2) + 0.164 | inverse of the above equation
SEER to SEER2 HP system | SEER2 = 0.623 (SEER) + 5.342 | Solaris Technical, LLC. 2022. "Crosswalk Methods for HVAC Efficiency Test Ratings via Appendix M to Appendix M1." Prepared for San Diego Gas and Electric (SDG&E) & Southern California Edison (SCE). November 2.
SEER2 to SEER HP system | SEER = 1.605 (SEER2) - 8.575 | inverse of the above equation
|  | Alternative method from FSEC that also includes HSPF conversions | https://support.energygauge.com/support/solutions/articles/12000091241-modeling-of-seer2-hspf2-and-how-it-compares-to-seer-hspf

## COP_calc
[6 empty] | EER = −0.02 × SEER² + 1.12 × SEER |  |  |  | approximation used for part load COP from SEER |  |  |  | approximation COP = HSPF x 0.293
|  | Measure Tiers |  | (refer to CDU folder for Brushless Fan) | [13 empty] | This equation was not used, though it should have been. Use this for the next revision of this measure.
Std Baseline Consideration | system type based on std cases | SEER | Pre/Std/Msr | # of Fan speed | SEER | EER | EER (full load minimum) | EER (full load AHRI) | COP1 (full load) | COP2 (if multi-speed, based on SEER) | HSPF (if Heat Pump) | AHRI HSPF | HSPF_final | equivalent heating COP | heating COP1 | heating COP2 (if multi-speed) | Note
|  | SEER 13 | Pre | 1 | 13 | 11.18 | 11 | 11.08 | 3.2258 | N/A | 7 |  | 7 | 2.051 | 2.051 | N/A | Thisis the pre-existing baseline for all equipment | 3.094
for this level, SEER 13 can be used for AC | Pkg | SEER 14 | Std | 1 | 14 | 11.76 | 11 |  | 3.2258 | N/A | 8 |  | 8 | 2.344 | 2.344 | N/A | This is the standard baseline for packaged systems, all sizes | 3.328
| Splt_45to65 | SEER 14.5 | Std | 1 | 14.5 | 12.035 | 11.7 |  | 3.4311 | N/A | 8.2 |  | 8.2 | 2.4026 | 2.4026 | N/A | This is the standard baseine for split systems 45-65 kbtuh | 3.3686
| Splt_lt45 | SEER 15 | Std | 1 | 15 | 12.3 | 12.2 |  | 3.5777 | N/A | 8.8 |  | 8.8 | 2.5784 | 2.5784 | N/A | This is the standard baseline for split systems < 45kbtuh | 3.4778
|  | SEER 16 | Msr | 2 | 16 | 12.8 | 12.2 |  | 3.5777 | 3.7537 | 9 |  | 9 | 2.637 | 2.637 | 2.637 |  | 3.51
|  | SEER 17 | Msr | 2 | 17 | 13.26 | 12.2 |  | 3.5777 | 3.8886 | 9.4 | 9.3309 | 9.4 | 2.7542 | 2.7542 | 2.7542 |  | 3.5682
|  | SEER 18 | Msr | 2 | 18 | 13.68 | 12.2 | 12.1 | 3.5777 | 4.0117 | 9.7 | 9.5837 | 9.518 | 2.7888 | 2.7888 | 2.7888 |  | 3.5838
|  | SEER 19 | Msr | 2 | 19 | 14.06 | 12.2 | 12.7 | 3.7243 | 4.1232 |  | 9.4522 | 9.518 | 2.7888 | 2.7888 | 2.7888 |  | 3.5838
|  | SEER 20 | Msr | 2 | 20 | 14.4 | 12.2 | 13.04 | 3.824 | 4.2229 |  | 9.9569 | 9.9569 | 2.9174 | 2.9174 | 2.9174 |  | 3.6355
|  | SEER 21 | Msr | 2 | 21 | 14.7 | 12.2 | 13.43 | 3.9384 | 4.3109 |  | 10.5486 | 10.5486 | 3.0907 | 3.0907 | 3.0907 |  | 3.6892
Cases setup - the red values changed
| Heat pump case name | AC Case Name | :vfd_curve_name | :supplyfan_total_eff | :motor_eff |  | :cooling_coil_cop | :coil_type | :cooling_coil_cop2 | :heating_coil_cop (if HP)
| HSPF_7p0_SEER_13_Pre | SEER_13_Pre |  | 0.12 | 0.24 |  | 3.23 |  |  | 2.051
| HSPF_8p0_SEER_14_Std | SEER_14_Std |  | 0.12 | 0.24 |  | 3.23 |  |  | 2.344 | Only run this for heat pumps, because it is the same as the SEER_13_Pre run for Acs
| HSPF_8p2_SEER_14.5_Std | SEER_14.5_Std |  | 0.12 | 0.24 |  | 3.43 |  |  | 2.4026
| HSPF_8p8_SEER_15_Std | SEER_15_Std |  | 0.12 | 0.24 |  | 3.58 |  |  | 2.5784
| HSPF_9p0_SEER_16_Msr | SEER_16_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.58 | multispeed | 3.7537 | 2.637
| HSPF_9p4_SEER_17_Msr | SEER_17_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.58 | multispeed | 3.8886 | 2.7542
| HSPF_9p5_SEER_18_Msr | SEER_18_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.58 | multispeed | 4.0117 | 2.7888
| HSPF_9p5_SEER_19_Msr | SEER_19_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.72 | multispeed | 4.1232 | 2.7888
| HSPF_10p0_SEER_20_Msr | SEER_20_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.82 | multispeed | 4.2229 | 2.9174
| HSPF_10p5_SEER_21_Msr | SEER_21_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.94 | multispeed | 4.3109 | 3.0907
OLD RUNS
|  | Case Name | :vfd_curve_name | :supplyfan_total_eff | :motor_eff |  | :cooling_coil_cop | :coil_type | :heating_coil_cop (if HP)
|  | SEER_13_Pre |  | 0.12 | 0.24 |  | 3.28 |  | 2.344
|  | SEER_15_Std |  | 0.12 | 0.24 |  | 3.61 |  | 2.5784
|  | SEER_16_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.75 | multispeed | 2.637
|  | SEER_17_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 3.89 | multispeed | 2.7542
|  | SEER_18_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 4.01 | multispeed | 2.7888
|  | SEER_19_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 4.12 | multispeed | 2.7888
|  | SEER_20_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 4.22 | multispeed | 2.9174
|  | SEER_21_Msr | VFD_Fan_Curve | 0.25 | 0.5 |  | 4.31 | multispeed | 3.0907
Note on M5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: based on EERE-2014-BT-STD-0048-0029_attachment_1, page 5-11
This sheet was used to develop the modeling runs for the residential SEER rated measure. (SWHC049). The more exact equation should have been used for the HSPF to COP conversion.

## Cooling
Source: Cutler, D., J. Winkler, N. Kruis, C. Christtensen, M. Brandemuehl. (2013) Improved Modeling of Residential Air Conditioners and Heat Pumps for Energy Calculations. NREL.
https://www.nrel.gov/docs/fy13osti/56354.pdf
Cooling Curve | f(T) curve form
Capacity as a function of temperature (Table 18 column 1)
f(FF) curve form
Capacity as a function of flow fraction (Table 14 column 1)
Plot curve from Table 18 and Table 19, Temperature on X-axis
also for EIR, plot the inverse (1/EIR = COP)
|  |  | a | b | c | d | e | f
|  | Cap_fT | 1.5574 | -0.074448 | 0.003099 | 0.00146 | -4.1e-05 | -0.00042
|  | EIR_fT | -0.35045 | 0.11681 | -0.0034 | -0.001226 | 0.000601 | -0.000467
|  | Degree C |  | Degree F |  | Cooling
|  | T_EWB | T_ODB | T_EWB | T_ODB | Capacity coeff | EIR coeff | COP
EIR as a function of temperature (Table 19 column 1) |  | 14 | 24 | 57.2 | 75.2 | 0.9928 | 0.77833
|  | 17 | 24 | 62.6 | 75.2 | 1.0274 | 0.77894
|  | 19 | 24 | 66.2 | 75.2 | 1.0815 | 0.74534
|  | 22 | 24 | 71.6 | 75.2 | 1.2091 | 0.64395
|  | 14 | 35 | 57.2 | 95 | 0.91757 | 1.083
|  | 17 | 35 | 62.6 | 95 | 0.93833 | 1.0682
|  | 19 | 35 | 66.2 | 95 | 0.98316 | 1.0243
|  | 22 | 35 | 71.6 | 95 | 1.0969 | 0.9075
|  | 14 | 40 | 57.2 | 104 | 0.88009 | 1.2695
|  | 17 | 40 | 62.6 | 104 | 0.89455 | 1.2477
|  | 19 | 40 | 66.2 | 104 | 0.93519 | 1.1992
|  | 22 | 40 | 71.6 | 104 | 1.0426 | 1.0754
EIR as a function of flow fraction (Table 15 column 1)
|  | Degree C |  | Degree F |  | Cooling
|  | T_ODB | T_EWB | T_ODB | T_EWB | Capacity coeff | EIR coeff | COP
|  | 24 | 14 | 75.2 | 57.2 | 0.9928 | 0.77833
|  | 35 | 14 | 95 | 57.2 | 0.91757 | 1.083
|  | 40 | 14 | 104 | 57.2 | 0.88009 | 1.2695
|  | 45 | 14 | 113 | 57.2 | 0.84057 | 1.4861
|  | 24 | 17 | 75.2 | 62.6 | 1.0274 | 0.77894
|  | 35 | 17 | 95 | 62.6 | 0.93833 | 1.0682
|  | 40 | 17 | 104 | 62.6 | 0.89455 | 1.2477
|  | 45 | 17 | 113 | 62.6 | 0.84873 | 1.4573
|  | 24 | 19 | 75.2 | 66.2 | 1.0815 | 0.74534
|  | 35 | 19 | 95 | 66.2 | 0.98316 | 1.0243
|  | 40 | 19 | 104 | 66.2 | 0.93519 | 1.1992
|  | 45 | 19 | 113 | 66.2 | 0.88516 | 1.4041
|  | 24 | 22 | 75.2 | 71.6 | 1.2091 | 0.64395
|  | 35 | 22 | 95 | 71.6 | 1.0969 | 0.9075
|  | 40 | 22 | 104 | 71.6 | 1.0426 | 1.0754
|  | 45 | 22 | 113 | 71.6 | 0.9863 | 1.2733

## Heating
Source: Cutler, D., J. Winkler, N. Kruis, C. Christtensen, M. Brandemuehl. (2013) Improved Modeling of Residential Air Conditioners and Heat Pumps for Energy Calculations. NREL.
https://www.nrel.gov/docs/fy13osti/56354.pdf
Heating Curve
Capacity as a function of temperature (Table 18 column 4)
Capacity as a function of flow fraction (Table 14 column 4)
EIR as a function of temperature (Table 19 column 4)
EIR as a function of flow fraction (Table 15 column 4)

## SEER_&_COPs
Measure specifications | This was an attempt to use python code built to generate SEER from EER to iteratively find EER from SEER. It did not work.
| Table for base/measure case parameters | [5 empty] | (does this need multi too? For multi speed?)
| Tech Case | Pre/Std/Msr | # of Fan speed | SEER | COP1 | COP2 (if multi-speed) | HSPF (if Heat Pump) | heating COP1 | heating COP2
| SEER 10 | Pre | 1 | 10 | 2.9308 | N/A | 7.1
| SEER 11 | Pre | 1 | 11 | 3.2239 | N/A
| SEER 12 | Pre | 1 | 12 | 3.517 | N/A
| SEER 13 | Pre | 1 | 13 | 3.8101 | N/A | 8.2
| SEER 14 | Std | 1 | 14 | 4.1032 | N/A | 8.2
| SEER 15 | Msr | 1 | 15 | 4.3962 | N/A | 8.7
| SEER 16 | Msr | 2 | 16 | 3.857 | 4.7107 | 9
| SEER 17 | Msr | 2 | 17 | 4.1584 | 5.0207 | 9.4
| SEER 18 | Msr | 2 | 18 | 4.463 | 5.3336 | 9.7
| SEER 19 | Msr | 2 | 19 | 4.7709 | 5.6495
| SEER 20 | Msr | 2 | 20 | 5.082 | 5.9684
| SEER 21 | Msr | 2 | 21 | 5.3964 | 6.2904
[5 empty] | What is a good COP range? |  | lowest, 3
highest 4.5
[5 empty] | starting value 1 | SEER / 3.412 ?
[5 empty] | starting value 2 | 1 + (SEER / 3.412) ?
COP pairs possible based on Newton's method
(Bigladder Python pacakge resdx-master)
|  |  |  | Target SEER | starting value 1 | starting value 2 | COP 1 | COP 2
|  |  |  | 16 | 4.6893 | 5.6893 | 3.857 | 4.7107
|  |  |  | 17 | 4.9824 | 5.9824 | 4.1584 | 5.0207
|  |  |  | 18 | 5.2755 | 6.2755 | 4.463 | 5.3336
|  |  |  | 19 | 5.5686 | 6.5686 | 4.7709 | 5.6495
|  |  |  | 20 | 5.8617 | 6.8617 | 5.082 | 5.9684
|  |  |  | 21 | 6.1547 | 7.1547 | 5.3964 | 6.2904

## Turndown ratio
Manufacturer data
LowLoadCOP | HighLoadCOP | Low/High ratio
5.2 | 2.8 | 1.8571
5 | 2.6 | 1.9231
4 | 2.4 | 1.6667
3.5 | 1 | 3.5
4 | 2.4 | 1.6667
4 | 2.4 | 1.6667
5.4 | 2.8 | 1.9286
4 | 2.4 | 1.6667
5 | 2.6 | 1.9231
3.8 | 3 | 1.2667
3.6 | 2.4 | 1.5