## Suggested sizing
| Suggested sizing from Pete Jacobs and Robert Mowris - Revised by Jennifer McWilliams | [5 empty] | Need to look at heating loads to see if these are sufficient
Climate Zone | AC SFm tons cool capacity (one story) | AC MFm tons cool capacity | AC Dmo tons cool capacity | Gas Furnace SFm kBtuh heating capacity (one story) | Gas Furnace MFm kBtuh heating capacity | Gas Furnace Dmo kBtuh heating capacity | Heat Pump SFm kBtuh heating capacity (one story) | Heat Pump MFm kBtuh heating capacity | Heat Pump Dmo kBtuh heating/cooling capacity |  | Assumptions
1 | 2.5 | 2 | 3.5 | 80 | 60 | 80 | 28.5 | 22.8 | 39.9 | SFm | Assumes 400 ft2 per ton AC. HP =tons*0.95, GF 80kBtuh (4 ton) 100 kBtuh (5 ton)
2 | 2.5 | 2 | 3.5 | 80 | 60 | 80 | 28.5 | 22.8 | 39.9 |  | Assumes 5 tons for ≥100F CDD and 4 tons <100 CDD
3 | 2.5 | 2 | 2.5 | 80 | 60 | 80 | 28.5 | 22.8 | 28.5 |  | Heat pump heat cap = 12*tons*0.95
4 | 2.5 | 2 | 3.5 | 80 | 60 | 80 | 28.5 | 22.8 | 39.9 | MFm | Assumes 3.0 tons for ≥100F CDD and 2.5 tons <100 CDD
5 | 2.5 | 2 | 3 | 80 | 60 | 80 | 28.5 | 22.8 | 34.2 |  | Heat pump heat cap = 12*tons*0.95
6 | 2.5 | 2 | 3 | 80 | 60 | 80 | 28.5 | 22.8 | 34.2 | Dmo | Note: Avergage floor area 1240 ft2. 3.5 tons and 55 kBtuh furnace and 12*tons*0.95 heat pump heat cap
7 | 2.5 | 2 | 2.5 | 80 | 60 | 80 | 28.5 | 22.8 | 28.5 |  | Notes: Manufactured Home Cooling Equipment Sizing Guidlines For ENERGY STAR® qualified manufactured homes and homes built to the HUD standards
8 | 2.5 | 2 | 2.5 | 80 | 60 | 80 | 28.5 | 22.8 | 28.5 |  | https://www.energystar.gov/sites/default/files/asset/document/SizingGuidelines_0.pdf
9 | 2.5 | 2 | 2.5 | 80 | 60 | 80 | 28.5 | 22.8 | 28.5
10 | 3 | 2.5 | 3 | 100 | 80 | 80 | 34.2 | 28.5 | 34.2 |  | The two story SFm house has double the capacity of a one story house
11 | 3 | 2.5 | 4 | 100 | 80 | 80 | 34.2 | 28.5 | 45.6
12 | 3 | 2.5 | 3.5 | 100 | 80 | 80 | 34.2 | 28.5 | 39.9 | 2024-06-28 | Jennifer added Mobile Home tab based on the Energy Star sizing document referenced in that tab.
13 | 3 | 2.5 | 4 | 100 | 80 | 80 | 34.2 | 28.5 | 45.6 |  | The sizing in column D was updated based on that work, but is probably a little undersized since the Energy Star document refers to HVAC sizing for new mobile homes. We should apply some factor to account for less insulated building shells of older mobile homes.
14 | 3 | 2.5 | 5 | 100 | 80 | 80 | 34.2 | 28.5 | 57 |  | Column J references column D, so it was also updated at this time, but needs to be adjusted for HDD which are different from CDD
15 | 3 | 2.5 | 5 | 100 | 80 | 80 | 34.2 | 28.5 | 57 |  | I added one ton to each CZ capacity to account for the older age homes
16 | 3 | 2.5 | 3.5 | 100 | 80 | 80 | 34.2 | 28.5 | 39.9 | 2024-07-01 | According to the 2010-12 HVAC QI installation evaluation, systems that did not go through the program are 13% oversized while those in the program are only 10% oversized
This is based on a sample of 50 participants and 50 non-participants where a manual J was performed in the evaluation and compared to the system size.
Climate Zone | AC SFm SF/ton cool capacity (one story) | AC MFm tons SF/ton cool capacity | AC Dmo SF/ton cool capacity | Gas Furnace SFm Btu/hr-SF (one story) | Gas Furnace MFm Btu/hr-SF | Gas Furnace DMo Btu/hr-SF | Heat Pump SFm Btu/hr-SF compressor heating capacity (one story) | Heat Pump MFm Btu/hr-SF compressor heating capacity | Heat Pump Dmo Btu/hr-SF compressor heating capacity |  | Report | https://www.calmac.org/publications/FINAL_HVAC_Impact_Evaluation_WO32_Report_28Jan2015_Volume1_Report.pdf
1 | 581.6 | 512 | 354.8571 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 32.1256 |  | Looking at the data another way, the non-participants had average size of 500 sq ft per ton in climate zones 8-14
2 | 581.6 | 512 | 354.8571 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 32.1256 |  | The homes in this study were all existing not new construction
3 | 581.6 | 512 | 496.8 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 22.9469 |  | note, the DNV study did not include 1.15 or 1.25 sizing factors. If they had, the participants would have been right sized and non-participants would have been only 3% oversized
4 | 581.6 | 512 | 354.8571 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 32.1256 |  | I've adusted the sizes so the sq ft per ton is 450 in CZs 8-16
5 | 581.6 | 512 | 414 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 27.5362
6 | 581.6 | 512 | 414 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 27.5362
7 | 581.6 | 512 | 496.8 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 22.9469
8 | 581.6 | 512 | 496.8 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 22.9469
9 | 581.6 | 512 | 496.8 | 55.0206 | 58.5938 | 64.4122 | 19.6011 | 22.2656 | 22.9469
10 | 484.6667 | 409.6 | 414 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 27.5362
11 | 484.6667 | 409.6 | 310.5 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 36.715
12 | 484.6667 | 409.6 | 354.8571 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 32.1256
13 | 484.6667 | 409.6 | 310.5 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 36.715
14 | 484.6667 | 409.6 | 248.4 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 45.8937
15 | 484.6667 | 409.6 | 248.4 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 45.8937
16 | 484.6667 | 409.6 | 354.8571 | 68.7758 | 78.125 | 64.4122 | 23.5213 | 27.832 | 32.1256
Energy Plus Autosize -- these are clearly our of the ballpark. Manual J gave 650 sq ft per ton: these are more than double except for mobile homes in higher CZs | [12 empty] | with 1.8 sizing factor applied
Climate Zone | AC SFm SF/ton cool capacity (one story) | AC MFm tons SF/ton cool capacity | AC Dmo SF/ton cool capacity | Gas Furnace SFm Btu/hr-SF (one story) | Gas Furnace MFm Btu/hr-SF | Gas Furnace DMo Btu/hr-SF | Heat Pump SFm Btu/hr-SF compressor heating capacity (one story) | Heat Pump MFm Btu/hr-SF compressor heating capacity | Heat Pump Dmo Btu/hr-SF compressor heating capacity | AC SFm SF/ton cool capacity (2 story DXGF) | Gas Furnace SFm Btu/hr-SF (two story) | Heat Pump story Btu/hr-SF compressor heating capacity (two story) | Climate Zone | AC SFm SF/ton cool capacity (one story) | AC MFm tons SF/ton cool capacity | AC Dmo SF/ton cool capacity
1 | 4080 | 4078.914 | 2259.446 | 7.6 | 7.3781 | 13.7785 | 2720 | 2724.1053 | 1506.1718 | 1843 | 33.8 | 1224 | 1 | 2266.6667 | 2266.0633 | 1255.2478
2 | 1542 | 1913.2091 | 1092.7236 | 15.7 | 12.7141 | 22.4238 | 1192 | 1421.9966 | 832.9455 | 1064 | 44.9 | 828 | 2 | 856.6667 | 1062.8939 | 607.0686
3 | 1540 | 1930.2338 | 1077.0676 | 18 | 13.6424 | 25.7149 | 1441 | 1291.0603 | 717.9856 | 1021 | 54.2 | 982 | 3 | 855.5556 | 1072.3521 | 598.3709
4 | 1481 | 1819.4692 | 1112.2546 | 16.4 | 12.8331 | 22.3117 | 1128 | 1361.463 | 828.5873 | 1093 | 43.7 | 839 | 4 | 822.7778 | 1010.8162 | 617.9192
5 | 1441 | 1959.7872 | 1059.1362 | 19.1 | 13.3156 | 26.0084 | 961 | 1306.4167 | 706.0326 | 982 | 56.1 | 653 | 5 | 800.5556 | 1088.7706 | 588.409
6 | 1780 | 1968.7021 | 1190.3882 | 16.2 | 13.128 | 24.2768 | 1186 | 1320.8067 | 793.5267 | 1216 | 47.5 | 805 | 6 | 988.8889 | 1093.7234 | 661.3268
7 | 1456 | 1916.4769 | 1009.5161 | 20.3 | 12.2465 | 29.5009 | 993 | 1404.5563 | 682.1653 | 1155 | 49.7 | 803 | 7 | 808.8889 | 1064.7094 | 560.8423
8 | 1380 | 1557.8096 | 1006.6945 | 20.3 | 15.0853 | 27.5793 | 991 | 1161.3839 | 729.359 | 1119 | 47.1 | 847 | 8 | 766.6667 | 865.4498 | 559.2747
9 | 1026 | 1400.35 | 783.2421 | 25.2 | 15.7326 | 32.1804 | 694 | 1046.1218 | 543.6257 | 883 | 57.9 | 599 | 9 | 570 | 777.9722 | 435.1345
10 | 2617.4852 | 1390.2153 | 951.186 | 7.577 | 14.8999 | 21.9248 | 2248.0228 | 1143.1687 | 776.9036 | 1253.4103 | 16.2188 | 1050.2363 | 10 | 1454.1584 | 772.3418 | 528.4367
11 | 2022.3652 | 1184.414 | 702.5195 | 10.8274 | 20.3265 | 32.0195 | 1607.1697 | 901.8572 | 542.6324 | 1100.5274 | 19.6662 | 883.9014 | 11 | 1123.5362 | 658.0078 | 390.2886
12 | 2523.7022 | 1706.814 | 842.3944 | 8.4806 | 12.1492 | 26.5686 | 2066.9705 | 1474.4887 | 659.7726 | 1270.0517 | 16.8566 | 1039.9144 | 12 | 1402.0568 | 948.23 | 467.9969
13 | 1831.0658 | 978.7877 | 745.8089 | 11.4377 | 22.993 | 29.867 | 1516.1134 | 754.1793 | 580.6069 | 1024.6823 | 20.7316 | 836.4596 | 13 | 1017.2588 | 543.7709 | 414.3383
14 | 1937.0794 | 1216.549 | 787.032 | 9.0674 | 16.2603 | 22.7315 | 1653.5207 | 1046.2378 | 659.5982 | 1085.7435 | 16.235 | 923.5507 | 14 | 1076.1552 | 675.8605 | 437.24
15 | 1452.9468 | 929.4808 | 593.6874 | 13.7401 | 22.845 | 34.4382 | 1233.2264 | 754.8303 | 492.1817 | 903.9856 | 22.3507 | 758.6385 | 15 | 807.1926 | 516.3782 | 329.8263
16 | 2987.2868 | 1288.3606 | 785.2446 | 8.6275 | 18.8028 | 33.4736 | 2070.6863 | 875.9222 | 533.7047 | 1337.8631 | 19.527 | 914.8972 | 16 | 1659.6038 | 715.7559 | 436.247
Suggested E+ oversize factor
Climate Zone | AC SFm SF/ton cool capacity (one story) | AC MFm | AC Dmo | Gas Furnace SFm Btu/hr-SF (one story) | Gas Furnace MFm | Gas Furnace DMo | Heat Pump SFm Btu/hr-SF compressor heating capacity (one story) | Heat Pump MFm | Heat Pump Dmo | AC SFm (two story DXGF) | Gas Furnace SFm (two story) | Heat Pump SFm (two story)
1 | 7.0116 | 7.9666 | 6.3672 | 7.2072 | 7.9415 | 4.6748 | 4.6741 | 5.3205 | 4.2445 | 3.1689 | 3.2587 | 2.1034
2 | 2.6501 | 3.7367 | 3.0794 | 3.5088 | 4.6085 | 2.8725 | 2.0486 | 2.7773 | 2.3473 | 1.8292 | 2.4502 | 1.4228
3 | 2.6466 | 3.77 | 2.168 | 3.0651 | 4.295 | 2.5049 | 2.4773 | 2.5216 | 1.4452 | 1.7557 | 2.0305 | 1.6878
4 | 2.5448 | 3.5536 | 3.1344 | 3.3613 | 4.5658 | 2.8869 | 1.9382 | 2.6591 | 2.335 | 1.8787 | 2.5197 | 1.4424
5 | 2.4773 | 3.8277 | 2.5583 | 2.8777 | 4.4004 | 2.4766 | 1.6514 | 2.5516 | 1.7054 | 1.6878 | 1.9608 | 1.1224
6 | 3.0586 | 3.8451 | 2.8754 | 3.3898 | 4.4632 | 2.6532 | 2.0389 | 2.5797 | 1.9167 | 2.0912 | 2.3155 | 1.3839
7 | 2.5017 | 3.7431 | 2.032 | 2.7119 | 4.7845 | 2.1834 | 1.7065 | 2.7433 | 1.3731 | 1.9862 | 2.2161 | 1.3809
8 | 2.3716 | 3.0426 | 2.0264 | 2.7119 | 3.8842 | 2.3355 | 1.7039 | 2.2683 | 1.4681 | 1.9243 | 2.3392 | 1.4561
9 | 1.7626 | 2.7351 | 1.5766 | 2.2 | 3.7244 | 2.0016 | 1.1928 | 2.0432 | 1.0943 | 1.5172 | 1 | 1.0304
10 | 5.4014 | 3.3941 | 2.2976 | 9.0783 | 5.2433 | 2.9379 | 4.639 | 2.7909 | 1.8766 | 2.5871 | 4.2421 | 2.1677
11 | 4.1733 | 2.8916 | 2.2626 | 6.353 | 3.8435 | 2.0117 | 3.3166 | 2.2018 | 1.7476 | 2.2715 | 3.4985 | 1.8244
12 | 5.2079 | 4.167 | 2.3739 | 8.111 | 6.4305 | 2.4244 | 4.2654 | 3.5998 | 1.8593 | 2.6215 | 4.0816 | 2.1464
13 | 3.7786 | 2.3896 | 2.402 | 6.014 | 3.3978 | 2.1566 | 3.1286 | 1.8413 | 1.8699 | 2.115 | 3.3187 | 1.7265
14 | 3.9974 | 2.9701 | 3.1684 | 7.5861 | 4.8047 | 2.8336 | 3.4122 | 2.5543 | 2.6554 | 2.241 | 4.2379 | 1.9063
15 | 2.9983 | 2.2692 | 2.3901 | 5.0063 | 3.4198 | 1.8704 | 2.5449 | 1.8428 | 1.9814 | 1.8659 | 3.0783 | 1.5659
16 | 6.1646 | 3.1454 | 2.2129 | 7.9729 | 4.155 | 1.9243 | 4.2731 | 2.1385 | 1.504 | 2.7614 | 3.5234 | 1.8884

## SFM QI eval
Report | https://www.calmac.org/publications/FINAL_HVAC_Impact_Evaluation_WO32_Report_28Jan2015_Volume1_Report.pdf
Apendicies | https://www.calmac.org/publications/FINAL_HVAC_Impact_Evaluation_WO32_Report_28Jan2015_Volume2_Appendices.pdf | [11 empty] | All parts were SCE
non parts had PGE, SCE and SDGE
|  |  | CZ8 | CZ9 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  | participants | 6 | 8 | 26 |  |  | 1 | 3 | 6
|  | non-participants | 2 | 7 | 14 | 4 | 12 | 9 | 2
Non-parts
| SiteID | CZ | floor area | Man J Tons | Actual Tons | Tonnage Difference Between Manual J and Installed ( > 0 oversized, < 0 undersized) | sq ft per ton Man J | sq ft per ton actual
| 51 | 10 | 2610 | 2.45 | 4 | 1.55 | 1065.3061 | 652.5
| 52 | 10 | 2784 | 2.22 | 4 | 1.78 | 1254.0541 | 696
| 53 | 10 | 1470 | 3.06 | 3 | -0.06 | 480.3922 | 490 |  |  | Row Labels | Average of sq ft per ton Man J | Average of sq ft per ton actual | Count of SiteID
| 54 | 10 | 2660 | 1.84 | 5 | 3.16 | 1445.6522 | 532 |  |  | 8 | 644.4218 | 476.5 | 2
| 55 | 10 | 3150 | 1.69 | 4 | 2.31 | 1863.9053 | 787.5 |  |  | 9 | 698.3498 | 436.0323 | 7
| 56 | 9 | CZ8: 1480; CZ9: 2.13; CZ10: 3; CZ13: 493.3333; CZ16: 10 | 797.068 | 558.1395 | 14
| 57 | 10 | 1352 | 2.73 | 3.5 | 0.77 | 495.2381 | 386.2857 |  |  | 11 | 730.2836 | 779.2333 | 4
| 58 | 10 | 1413 | 3 | 3 | 0 | 471 | 471 |  |  | 12 | 573.336 | 458.8233 | 12
| 59 | 10 | 1386 | 1.73 | 3 | 1.27 | 801.1561 | 462 |  |  | 13 | 439.9712 | 445.0556 | 9
| 60 | 10 | 2755 | 4.35 | 3 | -1.35 | 633.3333 | 918.3333 |  |  | 14 | 617.5288 | 466 | 2
| 61 | 10 | 1165 | 3.17 | 3 | -0.17 | 367.5079 | 388.3333 |  |  | Grand Total | 647.0942 | 509.6218 | 50
| 62 | 13 | 1252 | 2.83 | 2.5 | -0.33 | 442.4028 | 500.8
| 63 | 10 | 1594 | 3.47 | 4 | 0.53 | 459.366 | 398.5
| 64 | 10 | 1488 | 3.32 | 3 | -0.32 | 448.1928 | 496
| 65 | 9 | 1880 | 2.9 | 3.5 | 0.6 | 648.2759 | 537.1429
| 66 | 8 | 2096 | 2.45 | 4 | 1.55 | 855.5102 | 524
| 67 | 9 | 1518 | 1.96 | 4 | 2.04 | 774.4898 | 379.5
| 68 | 14 | 2000 | 5.39 | 4 | -1.39 | 371.0575 | 500
| 69 | 9 | 1625 | 2.4 | 4 | 1.6 | 677.0833 | 406.25
| 70 | 9 | 740 | 1 | 2.5 | 1.5 | 740 | 296
| 71 | 10 | 2865 | 4.08 | 5 | 0.92 | 702.2059 | 573
| 72 | 13 | 1584 | 2.64 | 2.5 | -0.14 | 600 | 633.6
| 73 | 13 | 1641 | 2.82 | 3 | 0.18 | 581.9149 | 547
| 74 | 9 | 1200 | 2.31 | 3 | 0.69 | 519.4805 | 400
| 75 | 9 | 1080 | 1.3 | 2 | 0.7 | 830.7692 | 540
| 76 | 8 | 1716 | 3.96 | 4 | 0.04 | 433.3333 | 429
| 77 | 10 | 2250 | 3.35 | 4 | 0.65 | 671.6418 | 562.5
| 78 | 14 | 1080 | 1.25 | 2.5 | 1.25 | 864 | 432
| 79 | 13 | 2282 | 7.18 | 5 | -2.18 | 317.8273 | 456.4
| 80 | 13 | 1434 | 4.18 | 4 | -0.18 | 343.0622 | 358.5
| 81 | 13 | 1928 | 5.98 | 5 | -0.98 | 322.408 | 385.6
| 82 | 12 | CZ8: 1125; CZ9: 2.14; CZ10: 3; CZ12: 525.7009
| 83 | 11 | 2026 | 7.12 | 5 | -2.12 | 284.5506 | 405.2
| 84 | 12 | 1421 | 2.95 | 3.5 | 0.55 | 481.6949 | 406
| 85 | 13 | 1526 | 3.45 | 3.5 | 0.05 | 442.3188 | 436
| 86 | 12 | 800 | 2.25 | 2.5 | 0.25 | 355.5556 | 320
| 87 | 12 | 1600 | 3.16 | 3 | -0.16 | 506.3291 | 533.3333
| 88 | 13 | 1065 | 2.1 | 3 | 0.9 | 507.1429 | 355
| 89 | 12 | CZ9: 2.76; CZ10: 3; CZ11: 0.24
| 90 | 12 | 1850 | 1.72 | 3 | 1.28 | 1075.5814 | 616.6667
| 91 | 12 | 1274 | 2.63 | 3 | 0.37 | 484.4106 | 424.6667
| 92 | 11 | 2000 | 3.75 | 3 | -0.75 | 533.3333 | 666.6667
| 93 | 12 | 2400 | 3.82 | 5 | 1.18 | 628.2723 | 480
| 94 | 12 | 1414 | 1.64 | 3 | 1.36 | 862.1951 | 471.3333
| 95 | 12 | 1204 | 3.44 | 3 | -0.44 | 350 | 401.3333
| 96 | 11 | 3992 | 2.8 | 5 | 2.2 | 1425.7143 | 798.4
| 97 | 12 | 2622 | 3.83 | 5 | 1.17 | 684.5953 | 524.4
| 98 | 12 | 1642 | 4.66 | 4 | -0.66 | 352.3605 | 410.5
| 99 | 11 | 1870 | 2.76 | 1.5 | -1.26 | 677.5362 | 1246.6667 | This should be removed as an outlier
| 100 | 13 | 1663 | 4.13 | 5 | 0.87 | 402.6634 | 332.6
|  | average | 1774.9388 | 3.085 | 3.54 | 0.43792 | 647.0942 | 509.6218
|  | median | 1600 | 2.825 | 3.25 | 0.54 | 529.5171 | 475.6667
[7 empty] | sq ft per ton Man J | sq ft per ton actual

## Mobile Home
HUD equipment sizing zone by CZ from 2005. This applies to HUD homes built 2000 or later. For our EX vintage, we should increase the sizing due to higher home loads from lower insulation levels.
https://www.energystar.gov/sites/default/files/asset/document/SizingGuidelines_0.pdf
CZ | value | source
1 | 33 | map | Row Labels | Average of value | HUD Cooling capacity (tons) for 1240 sq ft mobile home
1 | 25 | map | 1 | 29 | 2.5
2 | 25 | map | 2 | 31 | 2.5
2 | 32 | Ukiah | 3 | 8 | 1.5
2 | 32 | Santa Rosa | 4 | 34.5 | 2.5
2 | 35 | Napa | 5 | 14 | 2
3 | 9 | Oakland | 6 | 15 | 2
3 | 7 | San Francisco | 7 | 11 | 1.5
4 | 24 | San Jose | 8 |  | 1.5 | assumed same as CZ 7 and 9
4 | 45 | Paso Robles | 9 | 9 | 1.5
5 | 11 | Santa Maria | 10 | 22.3333 | 2
5 | 17 | San Juis Obispo | 11 | 52 | 3
6 | 21 | Long Beach | 12 | 43 | 2.5
6 | 9 | Santa Barbara | 13 | 56.5 | 3
7 | 11 | San Diego | 14 | 70 | 4
8 |  | Anaheim/Irvine | 15 | 70 | 4
9 | 9 | Los Angeles | 16 | 33.2857 | 2.5
10 | 47 | Riverside | Grand Total | 32.3143
10 | 13 | Escondido
10 | 7 | El Cajon
11 | 45 | map
11 | 59 | map
12 | 45 | map
12 | 39 | Merced
12 | 45 | Modesto
13 | 59 | map
13 | 54 | map
14 | 70 | map
15 | 70 | map
16 | 53 | map
16 | 9 | map
16 | 24 | map
16 | 15 | map
16 | 25 | map
16 | 47 | Victorville
16 | 60 | San Bernadino

## results-summary_SMm_CZ01-09
File Name | Conditioned Area (m2) | Conditioned Area (ft2)
CZ01/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ01/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ01/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ01/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ02/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ02/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ02/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ02/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ03/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ03/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ03/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ03/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ04/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ04/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ04/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ04/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ05/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ05/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ05/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ05/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ06/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ06/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ06/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ06/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ07/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ07/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ07/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ07/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ08/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ08/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ08/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ08/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
CZ09/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1454
CZ09/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2907
CZ09/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1454
CZ09/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2907
Sizing Factor Removed
| The model uses 1.8 sizing factor |  |  |  | Air Conditioner |  |  |  | Heat Pump |  |  | Furnace from below for comparison
File Name | Model DX Coil Cool Capacity (W) | Model DX Coil Cool Capacity (W) | Average of two orientations | 1.8 sizing factor removed | Model AC SFm SF/ton cool capacity | Model DX Coil Cool Capacity (tons) | AC Suggested Sizing (Tons) | Sizing Factor (dimensionless multiplier on design loads) | Model HP capacity (kBtu/hr) | Heat Pump Suggested Sizing (kBtu/hr) | HP Sizing Factor (dimensionless multiplier on design loads) | Model Gas Furnace SFm Btu/hr-SF | Furnace Suggested Sizing | Furnace Sizing Factor (dimensionless multiplier on design loads)
CZ01/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3030.77 | 3741.25 | 3386 | 1881.1111 | 2720 | 0.53486 | 2.5 | 4.6741 | 6.4184 | 46 | 7.1669
CZ01/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 16706.17 | 13390.63 | 15048.4 | 8360.2222 | 1224 | 2.3771 | 5 | 2.1034 | 28.5251 | 92 | 3.2252
CZ01/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2020.35 | 2493.96 | 2257.2 | 1254 | 4080 | 0.35655 | 2.5 | 7.0116 |  |  |  | 7.6 | 80 | 7.2072
CZ01/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 11096.71 | 8880.63 | 9988.7 | 5549.2778 | 1843 | 1.5778 | 5 | 3.1689 |  |  |  | 33.8 | 160 | 3.2587
CZ02/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 7388.37 | 8062.85 | 7725.6 | 4292 | 1192 | 1.2204 | 2.5 | 2.0486 | 14.6443 | 46 | 3.1412
CZ02/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 23291.25 | 21201.83 | 22246.5 | 12359.1667 | 828 | 3.5141 | 5 | 1.4228 | 42.1695 | 92 | 2.1817
CZ02/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5721.45 | 6222.77 | 5972.1 | 3317.8333 | 1542 | 0.94337 | 2.5 | 2.6501 |  |  |  | 15.7 | 80 | 3.5088
CZ02/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 18113.1 | 16496.16 | 17304.6 | 9613.6667 | 1064 | 2.7335 | 5 | 1.8292 |  |  |  | 44.9 | 160 | 2.4502
CZ03/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 8490.03 | 9451.04 | 8970.5 | 4983.6111 | 1027 | 1.417 | 2.5 | 1.7643 | 17.0041 | 46 | 2.7052
CZ03/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 28825.73 | 25405.06 | 27115.4 | 15064.1111 | 679 | 4.2832 | 5 | 1.1673 | 51.3987 | 92 | 1.7899
CZ03/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5659.55 | 6300.17 | 5979.9 | 3322.1667 | 1540 | 0.9446 | 2.5 | 2.6466 |  |  |  | 18 | 80 | 3.0651
CZ03/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 19166.18 | 16891.65 | 18028.9 | 10016.0556 | 1021 | 2.8479 | 5 | 1.7557 |  |  |  | 54.2 | 160 | 2.0305
CZ04/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 7648.77 | 8682.28 | 8165.5 | 4536.3889 | 1128 | 1.2898 | 2.5 | 1.9382 | 15.4782 | 46 | 2.9719
CZ04/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 23412.92 | 20476.71 | 21944.8 | 12191.5556 | 839 | 3.4665 | 5 | 1.4424 | 41.5976 | 92 | 2.2117
CZ04/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5873.01 | 6565.48 | 6219.2 | 3455.1111 | 1481 | 0.9824 | 2.5 | 2.5448 |  |  |  | 16.4 | 80 | 3.3613
CZ04/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 17832.78 | 15862.92 | 16847.9 | 9359.9444 | 1093 | 2.6613 | 5 | 1.8787 |  |  |  | 43.7 | 160 | 2.5197
CZ05/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9010.36 | 10156.69 | 9583.5 | 5324.1667 | 961 | 1.5138 | 2.5 | 1.6514 | 18.1661 | 46 | 2.5322
CZ05/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 30177.44 | 26224.59 | 28201 | 15667.2222 | 653 | 4.4547 | 5 | 1.1224 | 53.4566 | 92 | 1.721
CZ05/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6006.41 | 6770.56 | 6388.5 | 3549.1667 | 1441 | 1.0091 | 2.5 | 2.4773 |  |  |  | 19.1 | 80 | 2.8777
CZ05/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 20068.77 | 17438.91 | 18753.8 | 10418.7778 | 982 | 2.9624 | 5 | 1.6878 |  |  |  | 56.1 | 160 | 1.9608
CZ06/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 7325 | 8199.62 | 7762.3 | 4312.3889 | 1186 | 1.2262 | 2.5 | 2.0389 | 14.7139 | 46 | 3.1263
CZ06/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 24752.58 | 20990.44 | 22871.5 | 12706.3889 | 805 | 3.6128 | 5 | 1.3839 | 43.3542 | 92 | 2.1221
CZ06/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4882.93 | 5465.96 | 5174.4 | 2874.6667 | 1780 | 0.81736 | 2.5 | 3.0586 |  |  |  | 16.2 | 80 | 3.3898
CZ06/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 16386.51 | 13886.18 | 15136.3 | 8409.0556 | 1216 | 2.391 | 5 | 2.0912 |  |  |  | 47.5 | 160 | 2.3155
CZ07/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 8717.13 | 9831.1 | 9274.1 | 5152.2778 | 993 | 1.465 | 2.5 | 1.7065 | 17.5796 | 46 | 2.6167
CZ07/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 25054.4 | 20788.84 | 22921.6 | 12734.2222 | 803 | 3.6208 | 5 | 1.3809 | 43.4492 | 92 | 2.1174
CZ07/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5940.34 | 6712.44 | 6326.4 | 3514.6667 | 1456 | 0.99934 | 2.5 | 2.5017 |  |  |  | 20.3 | 80 | 2.7119
CZ07/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 17286.73 | 14585.59 | 15936.2 | 8853.4444 | 1155 | 2.5173 | 5 | 1.9862 |  |  |  | 49.7 | 160 | 2.2161
CZ08/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9133.96 | 9442.61 | 9288.3 | 5160.1667 | 991 | 1.4672 | 2.5 | 1.7039 | 17.6065 | 46 | 2.6127
CZ08/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 24096.03 | 19380.02 | 21738 | 12076.6667 | 847 | 3.4338 | 5 | 1.4561 | 41.2056 | 92 | 2.2327
CZ08/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6456.57 | 6889.91 | 6673.2 | 3707.3333 | 1380 | 1.0541 | 2.5 | 2.3716 |  |  |  | 20.3 | 80 | 2.7119
CZ08/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 17991.05 | 14906.9 | 16449 | 9138.3333 | 1119 | 2.5983 | 5 | 1.9243 |  |  |  | 47.1 | 160 | 2.3392
CZ09/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 13095.41 | 13441.78 | 13268.6 | 7371.4444 | 694 | 2.0959 | 2.5 | 1.1928 | 25.1514 | 46 | 1.8289
CZ09/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 32843.73 | 28595.56 | 30719.6 | 17066.4444 | 599 | 4.8526 | 5 | 1.0304 | 58.2307 | 92 | 1.5799
CZ09/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 8767.81 | 9190.84 | 8979.3 | 4988.5 | 1026 | 1.4184 | 2.5 | 1.7626 |  |  |  | 25.2 | 80 | 2.2
CZ09/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 22723.66 | 19000.83 | 20862.2 | 11590.1111 | 883 | 3.2955 | 5 | 1.5172 |  |  |  | 57.9 | 80 | 1
| The model uses 1.8 sizing factor |  |  | Sizing factor removed |  |  |  | New sizing factor
File Name | Model Fuel Coil Heat Capacity (W) | Model Fuel Coil Heat Capacity (W) | Average of two orientations (W) | 1.8 sizing factor removed (W) | Model Fuel Coil Heat Capacity (kBtu/hr) | Model Gas Furnace SFm Btu/hr-SF | Furnace Suggested Sizing | Sizing Factor (dimensionless multiplier on design loads)
CZ01/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ01/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ01/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5241.48 | 6470.2 | 5856 | 3253 | 11.1 | 7.6 | 80 | 7.2072
CZ01/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 28788.84 | 23039.55 | 25914 | 14397 | 49.1 | 33.8 | 160 | 3.2587
CZ02/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ02/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ02/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 11500.1 | 12549.92 | 12025 | 6681 | 22.8 | 15.7 | 80 | 3.5088
CZ02/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 36065.61 | 32829.95 | 34448 | 19138 | 65.3 | 44.9 | 160 | 2.4502
CZ03/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ03/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ03/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 13062.77 | 14541.38 | 13802 | 7668 | 26.1 | 18 | 80 | 3.0651
CZ03/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 44237.46 | 38987.61 | 41613 | 23118 | 78.8 | 54.2 | 160 | 2.0305
CZ04/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ04/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ04/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 11783.85 | 13376.1 | 12580 | 6989 | 23.8 | 16.4 | 80 | 3.3613
CZ04/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 35796.66 | 31286.57 | 33542 | 18634 | 63.5 | 43.7 | 160 | 2.5197
CZ05/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ05/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ05/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 13788.16 | 15542.33 | 14665 | 8147 | 27.8 | 19.1 | 80 | 2.8777
CZ05/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 46069.53 | 40032.46 | 43051 | 23917 | 81.6 | 56.1 | 160 | 1.9608
CZ06/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ06/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ06/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 11759.35 | 13163.44 | 12461 | 6923 | 23.6 | 16.2 | 80 | 3.3898
CZ06/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 39463.02 | 33441.56 | 36452 | 20251 | 69.1 | 47.5 | 160 | 2.3155
CZ07/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ07/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ07/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 14619.16 | 16487.35 | 15553 | 8641 | 29.5 | 20.3 | 80 | 2.7119
CZ07/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 41696.94 | 34569.78 | 38133 | 21185 | 72.2 | 49.7 | 160 | 2.2161
CZ08/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ08/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ08/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 15311.14 | 15828.5 | 15570 | 8650 | 29.5 | 20.3 | 80 | 2.7119
CZ08/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 40051 | 32173.36 | 36112 | 20062 | 68.4 | 47.1 | 160 | 2.3392
CZ09/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ09/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ09/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 19072.26 | 19576.46 | 19324.36 | 10735.8 | 36.6 | 25.2 | 80 | 2.2
CZ09/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 47528.2 | 41359.71 | 44443.955 | 24691.1 | 84.2 | 57.9 | 80 | 1
File Name | Elec Coil Heat Capacity (W) | Elec Coil Heat Capacity (W) | Average
CZ01/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3030.77 | 3741.25 | 3386.01
CZ01/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 16706.17 | 13390.63 | 15048.4
CZ01/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ01/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ02/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 7388.37 | 8062.85 | 7725.61
CZ02/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 23291.25 | 21201.83 | 22246.54
CZ02/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ02/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ03/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 8490.03 | 9451.04 | 8970.535
CZ03/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 28825.73 | 25405.06 | 27115.395
CZ03/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ03/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ04/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 7648.77 | 8682.28 | 8165.525
CZ04/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 23412.92 | 20476.71 | 21944.815
CZ04/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ04/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ05/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9010.36 | 10156.69 | 9583.525
CZ05/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 30177.44 | 26224.59 | 28201.015
CZ05/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ05/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ06/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 7325 | 8199.62 | 7762.31
CZ06/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 24752.58 | 20990.44 | 22871.51
CZ06/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ06/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ07/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 8717.13 | 9831.1 | 9274.115
CZ07/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 25054.4 | 20788.84 | 22921.62
CZ07/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ07/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ08/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9133.96 | 9442.61 | 9288.285
CZ08/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 24096.03 | 19380.02 | 21738.025
CZ08/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ08/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ09/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 13095.41 | 13441.78 | 13268.595
CZ09/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 32843.73 | 28595.56 | 30719.645
CZ09/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ09/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql

## results-summary_SFm_CZ10-16
File Name | Conditioned Area (m2) | Conditioned Area (ft2)
CZ10/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ10/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ10/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ10/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
CZ11/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ11/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ11/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ11/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
CZ12/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ12/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ12/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ12/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
CZ13/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ13/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ13/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ13/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
CZ14/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ14/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ14/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ14/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
CZ15/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ15/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ15/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ15/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
CZ16/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 270.12 | 1453.7723
CZ16/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 540.12 | 2906.8988
CZ16/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 270.12 | 1453.7723
CZ16/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 540.12 | 2906.8988
Sizing Factor Removed
| The model uses 1.8 sizing factor |  |  |  | Air Conditioner |  |  |  | Heat Pump |  |  | Furnace from below for comparison
File Name | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | Average of two orientations (W) | 1.8 sizing factor removed (W) | Model AC SFm SF/ton cool capacity | Model DX Coil Cool Capacity (tons) | AC Suggested Sizing (Tons) | Sizing Factor (dimensionless multiplier on design loads) | Model HP capacity (kBtu/hr) | Heat Pump Suggested Sizing (kBtu/hr) | HP Sizing Factor (dimensionless multiplier on design loads) | Model Fuel Coil Heat Capacity (kBtu/hr) | Furnace Suggested Sizing (kBtu/hr) | Furnace Sizing Factor (dimensionless multiplier on design loads)
CZ10/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3807.16 | 4380.7 | 4093.93 | 2274.4056 | 2248.0228 | 0.64669 | 3 | 4.639 | 7.7603 | 34.2 | 4.4071
CZ10/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 19085.94 | 15958.38 | 17522.16 | 9734.5333 | 1050.2363 | 2.7679 | 6 | 2.1677 | 33.2142 | 68.4 | 2.0594
CZ10/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3294.33 | 3737.8 | 3516.065 | 1953.3694 | 2617.4852 | 0.55541 | 3 | 5.4014 |  |  |  | 11.0152 | 100 | 9.0783
CZ10/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 15938.57 | 13425.17 | 14681.87 | 8156.5944 | 1253.4103 | 2.3192 | 6 | 2.5871 |  |  |  | 47.1464 | 200 | 4.2421
CZ11/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 5272.08 | 6180.66 | 5726.37 | 3181.3167 | 1607.1697 | 0.90455 | 3 | 3.3166 | 10.8547 | 34.2 | 3.1507
CZ11/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 23418.58 | 18220.47 | 20819.525 | 11566.4028 | 883.9014 | 3.2887 | 6 | 1.8244 | 39.4646 | 68.4 | 1.7332
CZ11/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4195.17 | 4906.3 | 4550.735 | 2528.1861 | 2022.3652 | 0.71885 | 3 | 4.1733 |  |  |  | 15.7406 | 100 | 6.353
CZ11/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 18643.91 | 14798.98 | 16721.445 | 9289.6917 | 1100.5274 | 2.6414 | 6 | 2.2715 |  |  |  | 57.1677 | 200 | 3.4985
CZ12/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4024.62 | 4880.44 | 4452.53 | 2473.6278 | 2066.9705 | 0.70333 | 3 | 4.2654 | 8.44 | 34.2 | 4.0521
CZ12/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 20262.37 | 15129.79 | 17696.08 | 9831.1556 | 1039.9144 | 2.7953 | 6 | 2.1464 | 33.5439 | 68.4 | 2.0391
CZ12/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3311.18 | 3982.27 | 3646.725 | 2025.9583 | 2523.7022 | 0.57605 | 3 | 5.2079 |  |  |  | 12.3289 | 100 | 8.111
CZ12/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 16397.29 | 12581.7 | 14489.495 | 8049.7194 | 1270.0517 | 2.2888 | 6 | 2.6215 |  |  |  | 49.0004 | 200 | 4.0816
CZ13/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 5531.93 | 6608.65 | 6070.29 | 3372.3833 | 1516.1134 | 0.95888 | 3 | 3.1286 | 11.5066 | 34.2 | 2.9722
CZ13/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 24980.34 | 19020.37 | 22000.355 | 12222.4194 | 836.4596 | 3.4752 | 6 | 1.7265 | 41.7029 | 68.4 | 1.6402
CZ13/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4634.05 | 5418.29 | 5026.17 | 2792.3167 | 1831.0658 | 0.79395 | 3 | 3.7786 |  |  |  | 16.6278 | 100 | 6.014
CZ13/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 20428.5 | 15489.77 | 17959.135 | 9977.2972 | 1024.6823 | 2.8369 | 6 | 2.115 |  |  |  | 60.2647 | 200 | 3.3187
CZ14/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 5207.89 | 5923.81 | 5565.85 | 3092.1389 | 1653.5207 | 0.8792 | 3 | 3.4122 | 10.5504 | 34.2 | 3.2416
CZ14/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 22815.02 | 17036.41 | 19925.715 | 11069.8417 | 923.5507 | 3.1475 | 6 | 1.9063 | 37.7703 | 68.4 | 1.8109
CZ14/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4466.38 | 5035.81 | 4751.095 | 2639.4972 | 1937.0794 | 0.7505 | 3 | 3.9974 |  |  |  | 13.182 | 100 | 7.5861
CZ14/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 19288.08 | 14610.18 | 16949.13 | 9416.1833 | 1085.7435 | 2.6773 | 6 | 2.241 |  |  |  | 47.1935 | 200 | 4.2379
CZ15/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 6968.13 | 7957.35 | 7462.74 | 4145.9667 | 1233.2264 | 1.1788 | 3 | 2.5449 | 14.146 | 34.2 | 2.4176
CZ15/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 26274.32 | 22239.98 | 24257.15 | 13476.1944 | 758.6385 | 3.8317 | 6 | 1.5659 | 45.9808 | 68.4 | 1.4876
CZ15/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5954.5 | 6713.89 | 6334.195 | 3518.9972 | 1452.9468 | 1.0006 | 3 | 2.9983 |  |  |  | 19.975 | 100 | 5.0063
CZ15/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 22548.7 | 18165.24 | 20356.97 | 11309.4278 | 903.9856 | 3.2156 | 6 | 1.8659 |  |  |  | 64.9711 | 200 | 3.0783
CZ16/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3905.47 | 4983.61 | 4444.54 | 2469.1889 | 2070.6863 | 0.70207 | 3 | 4.2731 | 8.4249 | 34.2 | 4.0594
CZ16/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 22890.3 | 17338.06 | 20114.18 | 11174.5444 | 914.8972 | 3.1773 | 6 | 1.8884 | 38.1275 | 68.4 | 1.794
CZ16/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2696.6 | 3465.01 | 3080.805 | 1711.5583 | 2987.2868 | 0.48665 | 3 | 6.1646 |  |  |  | 12.5424 | 100 | 7.9729
CZ16/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 15952.4 | 11557.75 | 13755.075 | 7641.7083 | 1337.8631 | 2.1728 | 6 | 2.7614 |  |  |  | 56.7629 | 200 | 3.5234
File Name | Model Fuel Coil Heat Capacity (W) | Model Fuel Coil Heat Capacity (W) | Average of two orientations (W) | 1.8 sizing factor removed (W) | Model Gas Furnace SFm Btu/hr-SF | Model Fuel Coil Heat Capacity (kBtu/hr) | Furnace Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads)
CZ10/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ10/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ10/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5404.04 | 6218.14 | 5811.09 | 3228.3833 | 7.577 | 11.0152 | 100 | 9.0783
CZ10/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 27091.78 | 22652.33 | 24872.055 | 13817.8083 | 16.2188 | 47.1464 | 200 | 4.2421
CZ11/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ11/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ11/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7645.16 | 8962.71 | 8303.935 | 4613.2972 | 10.8274 | 15.7406 | 100 | 6.353
CZ11/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 33923.77 | 26393.8 | 30158.785 | 16754.8806 | 19.6662 | 57.1677 | 200 | 3.4985
CZ12/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ12/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ12/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5879.02 | 7129.18 | 6504.1 | 3613.3889 | 8.4806 | 12.3289 | 100 | 8.111
CZ12/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 29598.94 | 22101.34 | 25850.14 | 14361.1889 | 16.8566 | 49.0004 | 200 | 4.0816
CZ13/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ13/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ13/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7994.04 | 9549.97 | 8772.005 | 4873.3361 | 11.4377 | 16.6278 | 100 | 6.014
CZ13/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 36099.01 | 27486.27 | 31792.64 | 17662.5778 | 20.7316 | 60.2647 | 200 | 3.3187
CZ14/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ14/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ14/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6506.9 | 7401.4 | 6954.15 | 3863.4167 | 9.0674 | 13.182 | 100 | 7.5861
CZ14/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 28507.05 | 21286.76 | 24896.905 | 13831.6139 | 16.235 | 47.1935 | 200 | 4.2379
CZ15/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ15/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ15/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 9839.39 | 11236.2 | 10537.795 | 5854.3306 | 13.7401 | 19.975 | 100 | 5.0063
CZ15/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 37125.85 | 31425.17 | 34275.51 | 19041.95 | 22.3507 | 64.9711 | 200 | 3.0783
CZ16/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ16/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ16/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 5814.23 | 7419.29 | 6616.76 | 3675.9778 | 8.6275 | 12.5424 | 100 | 7.9729
CZ16/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 34078.23 | 25812.26 | 29945.245 | 16636.2472 | 19.527 | 56.7629 | 200 | 3.5234
File Name | Elec Coil Heat Capacity (W) | Elec Coil Heat Capacity (W)
CZ10/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3807.16 | 4380.7
CZ10/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 19085.94 | 15958.38
CZ10/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ10/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ11/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 5272.08 | 6180.66
CZ11/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 23418.58 | 18220.47
CZ11/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ11/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ12/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4024.62 | 4880.44
CZ12/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 20262.37 | 15129.79
CZ12/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ12/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ13/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 5531.93 | 6608.65
CZ13/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 24980.34 | 19020.37
CZ13/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ13/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ14/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 5207.89 | 5923.81
CZ14/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 22815.02 | 17036.41
CZ14/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ14/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ15/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 6968.13 | 7957.35
CZ15/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 26274.32 | 22239.98
CZ15/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ15/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ16/SFm&1&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3905.47 | 4983.61
CZ16/SFm&2&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 22890.3 | 17338.06
CZ16/SFm&1&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ16/SFm&2&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql

## results-summary_MFm
File Name | Conditioned Area (m2) | Conditioned Area (ft2)
CZ01/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ01/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ02/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ02/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ03/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ03/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ04/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ04/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ05/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ05/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ06/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ06/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ07/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ07/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ08/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ08/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ09/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ09/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ10/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ10/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ11/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ11/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ12/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ12/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ13/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ13/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ14/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ14/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ15/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ15/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
CZ16/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2283.19 | 1024.0012
CZ16/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2283.19 | 1024.0012
Sizing Factor Removed
| The model uses 1.8 sizing factor | [25 empty] | Air Conditioner |  |  |  | Heat Pump |  |  | Furnace from below for comparison
File Name | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | Average of all apartments (W) | 1.8 sizing factor removed (W) | Model AC SFm SF/ton cool capacity | Model DX Coil Cool Capacity (tons) | AC Suggested Sizing (Tons) | Sizing Factor (dimensionless multiplier on design loads) | Model HP capacity (kBtu/hr) | Heat Pump Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads) | Model Fuel Coil Heat Capacity (kBtu/hr) | Furnace Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads)
CZ01/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 437.45 | 1600.39 | 53.96 | 1483.3 | 359.34 | 1304.44 | 441.63 | 4654.2 | 56.22 | 4637.96 | 361.48 | 4644.34 | 440.98 | 4679.3 | 53.96 | 894.34 | 355.57 | 2603.19 | 357.72 | 2639.83 | 56.22 | 898.38 | 445.15 | 4683.39 | 1589.2808 | 882.9338 | 4078.914 | 0.25105 | 2 | 7.9666 |  |  |  | 7.5552 | 60 | 7.9415
CZ01/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 656.23 | 2400.79 | 80.95 | 2224.68 | 539.06 | 1940.63 | 662.49 | 6981.88 | 84.33 | 6957.52 | 542.26 | 6967.09 | 661.52 | 7019.54 | 80.95 | 1297.29 | 533.4 | 3905.11 | 536.62 | 3960.07 | 84.33 | 1302.5 | 667.78 | 7025.66 | 2379.695 | 1322.0528 | 2724.1053 | 0.3759 | 2 | 5.3205 | 4.5108 | 22.8 | 5.0545
CZ02/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1176.41 | 4702.38 | 952.57 | 4023.6 | 1224.51 | 4757 | 1160.34 | 7606.08 | 934.88 | 7090.19 | 1208.16 | 7612.85 | 1159.11 | 7616.36 | 933.69 | 3811.06 | 1216.77 | 4678.74 | 1218 | 4689.28 | 934.85 | 3817.52 | 1159.89 | 7635.13 | 3388.3071 | 1882.3928 | 1913.2091 | 0.53523 | 2 | 3.7367 |  |  |  | 13.0193 | 60 | 4.6085
CZ02/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1547.72 | 6267.08 | 1278.81 | 5417.09 | 1618.05 | 6307.26 | 1526.44 | 10360.65 | 1255.01 | 9663.21 | 1596.35 | 10371.55 | 1524.8 | 10356.54 | 1253.41 | 5130.45 | 1607.64 | 6201.38 | 1609.29 | 6215.36 | 1254.95 | 5139.15 | 1525.81 | 10382.22 | 4558.7592 | 2532.644 | 1421.9966 | 0.72012 | 2 | 2.7773 | 8.6414 | 22.8 | 2.6385
CZ03/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1163.76 | 4561.96 | 824.86 | 3913.11 | 1179.97 | 4213.18 | 1150.8 | 7756.62 | 812.25 | 7295.23 | 1166.87 | 7760.41 | 1151.26 | 7602.9 | 816.22 | 3109.05 | 1181.91 | 5549.5 | 1177.12 | 5544.68 | 811.91 | 3100.21 | 1146.7 | 7611.65 | 3358.4221 | 1865.79 | 1930.2338 | 0.53051 | 2 | 3.77 |  |  |  | 13.9698 | 60 | 4.295
CZ03/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1713.45 | 6843.51 | 1192.97 | 5870.15 | 1745.47 | 6320.29 | 1693.15 | 11635.9 | 1174.18 | 10943.75 | 1725.49 | 11641.59 | 1693.85 | 11405.29 | 1180.33 | 4663.97 | 1749.17 | 8324.93 | 1741.71 | 8317.7 | 1173.68 | 4650.7 | 1686.69 | 11418.42 | 5021.0975 | 2789.4986 | 1291.0603 | 0.79315 | 2 | 2.5216 | 9.5178 | 22.8 | 2.3955
CZ04/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1318.68 | 4914.1 | 1066.65 | 4194.11 | 1364.54 | 4959.84 | 1306.65 | 7824.53 | 1054.3 | 7263.67 | 1353.21 | 7824.12 | 1306.4 | 7837.05 | 1053.73 | 4047.37 | 1359.79 | 4920.02 | 1359.88 | 4921.29 | 1053.51 | 4047.74 | 1305.83 | 7851.97 | 3562.8742 | 1979.3745 | 1819.4692 | 0.5628 | 2 | 3.5536 |  |  |  | 13.1411 | 60 | 4.5658
CZ04/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1721.79 | 6456.09 | 1418.83 | 5617.15 | 1789.23 | 6546.71 | 1705.89 | 10591.73 | 1402.26 | 9841.81 | 1774.24 | 10588.34 | 1705.55 | 10597.39 | 1401.5 | 5419.9 | 1782.87 | 6492.4 | 1782.98 | 6494.03 | 1401.2 | 5420.41 | 1704.79 | 10617.74 | 4761.4512 | 2645.2507 | 1361.463 | 0.75213 | 2 | 2.6591 | 9.0256 | 22.8 | 2.5261
CZ05/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1184.5 | 4216.07 | 739.86 | 3444.61 | 1224.76 | 4191.19 | 1190.63 | 7919.53 | 745.79 | 7526.36 | 1230.79 | 7907.22 | 1189.87 | 7707.35 | 739.87 | 3127.23 | 1219.05 | 4919.14 | 1225.1 | 4941.94 | 745.79 | 3122.45 | 1196 | 7731.56 | 3307.7775 | 1837.6542 | 1959.7872 | 0.52251 | 2 | 3.8277 |  |  |  | 13.6351 | 60 | 4.4004
CZ05/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1776.89 | 6324.62 | 1109.89 | 5167.35 | 1837.29 | 6287.3 | 1786.09 | 11880.27 | 1118.78 | 11290.48 | 1846.33 | 11861.82 | 1784.95 | 11561.99 | 1109.89 | 4691.24 | 1828.73 | 7379.31 | 1837.8 | 7413.53 | 1118.78 | 4684.06 | 1794.15 | 11598.3 | 4962.0767 | 2756.7093 | 1306.4167 | 0.78382 | 2 | 2.5516 | 9.4059 | 22.8 | 2.424
CZ06/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1236.82 | 4461.22 | 858 | 3872.44 | 1263.62 | 4169.06 | 1227.18 | 7358.55 | 848.89 | 6902.62 | 1253.95 | 7371.2 | 1227 | 7222.23 | 848.58 | 3127.47 | 1259.28 | 5374.8 | 1262.86 | 5410.85 | 851.89 | 3138.45 | 1230.54 | 7249.67 | 3292.7987 | 1829.3326 | 1968.7021 | 0.52014 | 2 | 3.8451 |  |  |  | 13.4431 | 60 | 4.4632
CZ06/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1820.82 | 6692.39 | 1261.4 | 5809.14 | 1863.48 | 6254.11 | 1806.55 | 10988.56 | 1248 | 10308.05 | 1849.24 | 11008.11 | 1806.29 | 10773.37 | 1247.47 | 4630.7 | 1857.08 | 8062.86 | 1862.37 | 8116.95 | 1252.36 | 4647.01 | 1811.52 | 10814.54 | 4908.0154 | 2726.6752 | 1320.8067 | 0.77528 | 2 | 2.5797 | 9.3034 | 22.8 | 2.4507
CZ07/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1051.34 | 4236.32 | 932.36 | 3816.03 | 1227.49 | 4204.92 | 1045.9 | 7810.65 | 925.64 | 7438.22 | 1221.38 | 7818.77 | 1043.6 | 7600.89 | 924.75 | 3607.95 | 1230.52 | 5263.28 | 1227.08 | 5330.31 | 923.57 | 3619.47 | 1040.34 | 7639.93 | 3382.5296 | 1879.1831 | 1916.4769 | 0.53431 | 2 | 3.7431 |  |  |  | 12.5404 | 60 | 4.7845
CZ07/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1363.03 | 5717.09 | 1201.13 | 5292.12 | 1528.07 | 5594.07 | 1355.41 | 10803.65 | 1191.74 | 10297.98 | 1519.93 | 10819.37 | 1352.4 | 10537.7 | 1190.65 | 4897.1 | 1531.64 | 7438.82 | 1527.15 | 7545.97 | 1188.97 | 4913.65 | 1348.02 | 10613.1 | 4615.365 | 2564.0917 | 1404.5563 | 0.72906 | 2 | 2.7433 | 8.7487 | 22.8 | 2.6061
CZ08/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1534.18 | 5336.35 | 1244.92 | 4520.24 | 1647.04 | 5406.22 | 1526.41 | 9445.17 | 1239.63 | 8819.49 | 1639.93 | 9458.3 | 1524.82 | 9224.35 | 1237.87 | 4428.31 | 1646.56 | 5921.81 | 1645.97 | 5977.04 | 1237.76 | 4435.56 | 1523.71 | 9249.97 | 4161.3171 | 2311.8428 | 1557.8096 | 0.65733 | 2 | 3.0426 |  |  |  | 15.4473 | 60 | 3.8842
CZ08/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1907.63 | 6918.61 | 1649.77 | 5988.25 | 2088.75 | 7002.2 | 1902.44 | 12850.19 | 1644.79 | 12044.38 | 2079.44 | 12923.63 | 1897.94 | 12525.42 | 1642.41 | 5864.41 | 2087.84 | 8294.63 | 2087.07 | 8376.62 | 1642.25 | 5995.13 | 1896.55 | 12651.35 | 5581.7375 | 3100.9653 | 1161.3839 | 0.88171 | 2 | 2.2683 | 10.5805 | 22.8 | 2.1549
CZ09/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1632.49 | 6105.18 | 1248.02 | 5175.22 | 1711.89 | 6159.4 | 1627.73 | 10415.06 | 1241.83 | 9706.12 | 1706.53 | 10418.09 | 1625.69 | 10289.61 | 1240.81 | 5087.71 | 1710.25 | 6979.98 | 1710.41 | 7047.13 | 1240.95 | 5089.3 | 1625.73 | 10306.35 | 4629.2283 | 2571.7935 | 1400.35 | 0.73125 | 2 | 2.7351 |  |  |  | 16.1102 | 60 | 3.7244
CZ09/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2096.01 | 7981.85 | 1674.58 | 6909.83 | 2214.05 | 8056.79 | 2089.75 | 14022.2 | 1666.27 | 13072.38 | 2207.11 | 14027.27 | 2087.14 | 13845.4 | 1664.9 | 6813.76 | 2211.82 | 9664.96 | 2212.03 | 9760.02 | 1665.09 | 6815.88 | 2087.2 | 13875.36 | 6196.7354 | 3442.6308 | 1046.1218 | 0.97885 | 2 | 2.0432 | 11.7463 | 22.8 | 1.941
CZ10/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2307.46 | 6283.69 | 1628.4 | 4914.92 | 2345 | 6293.9 | 2297.78 | 9733.12 | 1618.35 | 8909.64 | 2335.38 | 9761.17 | 2295.89 | 9596.09 | 1616.63 | 4680.62 | 2339.81 | 6222.91 | 2340.06 | 6229.78 | 1616.92 | 4618.54 | 2296.09 | 9629.26 | 4662.9754 | 2590.5419 | 1390.2153 | 0.73658 | 2.5 | 3.3941 |  |  |  | 15.2575 | 80 | 5.2433
CZ10/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2682.15 | 7514.35 | 1861.09 | 5848.99 | 2730.73 | 7527.12 | 2670.12 | 12325.52 | 1848.52 | 11299.19 | 2718.78 | 12367.71 | 2667.84 | 12012.7 | 1846.48 | 5561.66 | 2724.29 | 7439.87 | 2724.6 | 7448.25 | 1846.83 | 5705.93 | 2668.09 | 12055.43 | 5670.6767 | 3150.3759 | 1143.1687 | 0.89576 | 2.5 | 2.7909 | 10.7491 | 28.5 | 2.6514
CZ11/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2703.47 | 7490.66 | 1951.1 | 6078.99 | 2760.02 | 7546.01 | 2693.24 | 11179.71 | 1936.45 | 10024.81 | 2751.51 | 11198.77 | 2695.65 | 10922.95 | 1943.69 | 5993.31 | 2758.35 | 7096.73 | 2755.79 | 7283.11 | 1941.18 | 5991.4 | 2693.2 | 10966.8 | 5473.2042 | 3040.669 | 1184.414 | 0.86456 | 2.5 | 2.8916 |  |  |  | 20.8143 | 80 | 3.8435
CZ11/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3312.09 | 9312.46 | 2515.64 | 7927.33 | 3509.45 | 9582.69 | 3299.55 | 14932.15 | 2538.25 | 13389.7 | 3498.58 | 14957.5 | 3302.51 | 14555.65 | 2506.18 | 7885.68 | 3507.15 | 9957.92 | 3503.87 | 10233.95 | 2502.97 | 7883.19 | 3299.5 | 14597.78 | 7187.9892 | 3993.3273 | 901.8572 | 1.1354 | 2.5 | 2.2018 | 13.6252 | 28.5 | 2.0917
CZ12/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1453.14 | 5416.38 | 1105.62 | 4215.8 | 1634.86 | 5437.87 | 1435.26 | 8298.33 | 1090.28 | 7624.36 | 1631.45 | 8335.4 | 1433.43 | 8139.46 | 1086.3 | 3994.71 | 1627.45 | 5378.28 | 1628.66 | 5395.83 | 1089.49 | 4017.49 | 1436.47 | 8246.53 | 3798.0354 | 2110.0197 | 1706.814 | 0.59995 | 2.5 | 4.167 |  |  |  | 12.4408 | 80 | 6.4305
CZ12/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1584.65 | 6168.3 | 1196.78 | 4809.45 | 1789.6 | 6209.56 | 1566.05 | 9936.3 | 1179.22 | 9150.11 | 1784.89 | 10027.72 | 1564.01 | 9705.92 | 1174.79 | 4585.78 | 1781.15 | 6144.57 | 1782.58 | 6164.91 | 1178.36 | 4605.29 | 1567.45 | 9857.75 | 4396.4663 | 2442.4813 | 1474.4887 | 0.69448 | 2.5 | 3.5998 | 8.3337 | 28.5 | 3.4198
CZ13/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3807.99 | 8823.19 | 2941.24 | 7304.51 | 3837.4 | 8836.19 | 3805.4 | 12157.82 | 2937.34 | 10774.66 | 3836.2 | 12056.4 | 3804.7 | 12260.94 | 2932.43 | 7213.31 | 3830.77 | 8800.4 | 3836.43 | 8814.76 | 2937 | 7223.78 | 3809.08 | 12370.77 | 6623.0296 | 3679.4609 | 978.7877 | 1.0462 | 2.5 | 2.3896 |  |  |  | 23.5448 | 80 | 3.3978
CZ13/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4832.42 | 11450.35 | 3694.95 | 9441.6 | 4874.52 | 11468.54 | 4829 | 15985.88 | 3689.82 | 14286.18 | 4872.9 | 15989.39 | 4828.1 | 16218 | 3683.42 | 9320.99 | 4865.81 | 11421.19 | 4873.19 | 11440.21 | 3689.38 | 9334.83 | 4833.84 | 16367.22 | 8595.4887 | 4775.2715 | 754.1793 | 1.3578 | 2.5 | 1.8413 | 16.2932 | 28.5 | 1.7492
CZ14/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3032.02 | 7168.89 | 1975.23 | 5357.11 | 3088.56 | 7199.93 | 3031.81 | 10488.17 | 1976.09 | 9303.77 | 3088.98 | 10566.23 | 3030.84 | 10478.69 | 1968.47 | 5263.8 | 3081.17 | 6831.25 | 3088 | 6965.22 | 1975.6 | 5279.67 | 3037.71 | 10609.92 | 5328.6304 | 2960.3502 | 1216.549 | 0.84173 | 2.5 | 2.9701 |  |  |  | 16.6505 | 80 | 4.8047
CZ14/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3436.67 | 8144.63 | 2238.34 | 6106.67 | 3500.7 | 8186.33 | 3436.42 | 12347.18 | 2239.3 | 10974.78 | 3501.18 | 12474.36 | 3435.33 | 12261.73 | 2230.67 | 6009.25 | 3492.32 | 8430.12 | 3500.06 | 8617.24 | 2238.75 | 6027.37 | 3443.12 | 12432.64 | 6196.0483 | 3442.2491 | 1046.2378 | 0.97875 | 2.5 | 2.5543 | 11.745 | 28.5 | 2.4266
CZ15/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3898.62 | 9314.27 | 2740.87 | 7489.63 | 3982.49 | 9381.29 | 3894.21 | 13479.19 | 2737.04 | 11979.75 | 3977.87 | 13598.24 | 3892.01 | 13238.15 | 2736.76 | 7425.72 | 3982.14 | 9003 | 3982.56 | 9190.68 | 2737.1 | 7433.8 | 3892.27 | 13397.13 | 6974.3662 | 3874.6479 | 929.4808 | 1.1017 | 2.5 | 2.2692 |  |  |  | 23.3933 | 80 | 3.4198
CZ15/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4472.57 | 10839.76 | 3411.36 | 9018.52 | 4696.2 | 11030.19 | 4467.43 | 16868.55 | 3406.63 | 15036.87 | 4690.82 | 17150.86 | 4464.99 | 16486.03 | 3406.26 | 9010.03 | 4695.6 | 11787.36 | 4696.11 | 12266.19 | 3406.7 | 9422.43 | 4465.29 | 16917.08 | 8588.0763 | 4771.1535 | 754.8303 | 1.3566 | 2.5 | 1.8428 | 16.2792 | 28.5 | 1.7507
CZ16/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2120.77 | 6758.87 | 1495.37 | 5491.29 | 2174.37 | 6816.93 | 2102.56 | 11180.54 | 1476.64 | 10249.68 | 2156.55 | 11281.81 | 2101.13 | 10865.05 | 1475.03 | 5283.49 | 2169.1 | 6728.45 | 2168.56 | 6718.97 | 1473.44 | 5327.59 | 2099.64 | 11043.03 | 5031.6192 | 2795.344 | 1288.3606 | 0.79481 | 2.5 | 3.1454 |  |  |  | 19.2541 | 80 | 4.155
CZ16/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2971.65 | 9634.12 | 2178.89 | 8060.33 | 3069.69 | 9782.11 | 2946.08 | 16772.2 | 2158.7 | 15375.8 | 3051.47 | 16924.11 | 2944.08 | 16298.92 | 2156.35 | 7880.17 | 3068.69 | 9756.03 | 3060.79 | 9875.44 | 2154.04 | 7992.05 | 2941.98 | 16565.92 | 7400.8171 | 4111.565 | 875.9222 | 1.1691 | 2.5 | 2.1385 | 14.0287 | 28.5 | 2.0316
File Name | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Average of all apartments (W) | 1.8 sizing factor removed (W) | Model Gas Furnace SFm Btu/hr-SF | Model Fuel Coil Heat Capacity (kBtu/hr) | Furnace Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads)
CZ01/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1099.1 | 4021.08 | 135.57 | 3726.1 | 902.87 | 3250.38 | 1109.59 | 11693.97 | 141.24 | 11653.08 | 908.23 | 11669.23 | 1107.96 | 11757.04 | 135.58 | 2172.82 | 893.4 | 6540.7 | 898.79 | 6632.74 | 141.25 | 2181.54 | 1118.45 | 11767.3 | 3985.7504 | 2214.3058 | 7.3781 | 7.5552 | 60 | 7.9415
CZ01/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ02/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2257.85 | 9160.56 | 3109.76 | 7919.03 | 2360.96 | 9231.06 | 2226.81 | 15144.12 | 3051.87 | 14126.25 | 2329.29 | 15179.39 | 2224.34 | 15138.05 | 3047.97 | 7500.09 | 2345.77 | 9076.19 | 2348.18 | 9096.56 | 3051.73 | 7512.72 | 2225.57 | 15175.59 | 6868.3213 | 3815.734 | 12.7141 | 13.0193 | 60 | 4.6085
CZ02/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ03/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2528.4 | 10053.91 | 1756.24 | 8612.83 | 2559.7 | 9257.15 | 2498.41 | 17094.48 | 1728.58 | 16056.93 | 2530.41 | 17051.13 | 2499.44 | 16755.69 | 1737.63 | 6843.08 | 2565.15 | 12193.32 | 2554.18 | 12182.7 | 1727.84 | 6823.62 | 2488.91 | 16774.99 | 7369.78 | 4094.3222 | 13.6424 | 13.9698 | 60 | 4.295
CZ03/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ04/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2418.93 | 9073.86 | 3451.05 | 7894.73 | 2514.69 | 9201.28 | 2396.87 | 14886.38 | 3410.75 | 13832.35 | 2493.62 | 14881.71 | 2396.48 | 14894.34 | 3408.91 | 7617.5 | 2505.74 | 9124.94 | 2505.9 | 9127.24 | 3408.19 | 7618.2 | 2395.68 | 14922.94 | 6932.595 | 3851.4417 | 12.8331 | 13.1411 | 60 | 4.5658
CZ04/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ05/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2575.92 | 9168.7 | 1608.95 | 7490.25 | 2663.48 | 9114.27 | 2589.25 | 17222.63 | 1621.84 | 16366.01 | 2676.6 | 17195.31 | 2587.6 | 16761.22 | 1608.96 | 6800.12 | 2651.08 | 10697.28 | 2664.22 | 10746.91 | 1621.84 | 6789.74 | 2600.93 | 16813.86 | 7193.2071 | 3996.2262 | 13.3156 | 13.6351 | 60 | 4.4004
CZ05/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ06/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2630.99 | 9670.31 | 1822.64 | 8394 | 2692.64 | 9037.01 | 2610.36 | 15878.16 | 1803.29 | 14894.77 | 2672.07 | 15906.41 | 2609.98 | 15567.21 | 1802.52 | 6691.2 | 2683.39 | 11650.61 | 2691.03 | 11728.76 | 1809.58 | 6714.77 | 2617.55 | 15626.71 | 7091.915 | 3939.9528 | 13.128 | 13.4431 | 60 | 4.4632
CZ06/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ07/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 1953.76 | 8194.93 | 1721.68 | 7585.74 | 2190.33 | 8018.6 | 1942.84 | 15486.05 | 1708.21 | 14761.16 | 2178.66 | 15508.61 | 1938.52 | 15104.82 | 1706.65 | 7019.52 | 2195.45 | 10662.89 | 2189.01 | 10816.48 | 1704.24 | 7043.23 | 1932.25 | 15212.91 | 6615.6892 | 3675.3829 | 12.2465 | 12.5404 | 60 | 4.7845
CZ07/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ08/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2785.04 | 10101.08 | 2408.58 | 8742.72 | 3049.51 | 10223.11 | 2777.47 | 18761.1 | 2401.3 | 17584.54 | 3035.92 | 18868.32 | 2770.9 | 18286.94 | 2397.83 | 8561.92 | 3048.18 | 12110.04 | 3047.05 | 12229.75 | 2397.59 | 8752.76 | 2768.88 | 18470.79 | 8149.2217 | 4527.3454 | 15.0853 | 15.4473 | 60 | 3.8842
CZ08/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ09/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2874.65 | 10947.27 | 2296.66 | 9476.94 | 3036.58 | 11050.05 | 2866.06 | 19231.72 | 2285.27 | 17928.96 | 3027.06 | 19238.68 | 2862.48 | 18989.24 | 2283.39 | 9345.17 | 3033.51 | 13255.69 | 3033.8 | 13386.06 | 2283.65 | 9348.08 | 2862.56 | 19030.33 | 8498.9108 | 4721.6171 | 15.7326 | 16.1102 | 60 | 3.7244
CZ09/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ10/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3807.04 | 10666.14 | 2641.61 | 8302.23 | 3876.05 | 10684.26 | 3789.96 | 17495.29 | 2623.78 | 16038.39 | 3859.08 | 17555.17 | 3786.73 | 17051.26 | 2620.87 | 7894.38 | 3866.9 | 10560.41 | 3867.34 | 10572.31 | 2621.38 | 8099.16 | 3787.09 | 17111.91 | 8049.1142 | 4471.7301 | 14.8999 | 15.2575 | 80 | 5.2433
CZ10/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ11/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4870.56 | 13721.56 | 6052.39 | 11687.17 | 5161 | 14121.8 | 4852.12 | 22001.97 | 6106.78 | 19740.28 | 5145.02 | 22042.53 | 4856.47 | 21447.2 | 6029.62 | 11625.75 | 5157.62 | 14674.77 | 5152.8 | 15081.54 | 6021.92 | 11622.09 | 4852.04 | 21509.29 | 10980.5954 | 6100.3308 | 20.3265 | 20.8143 | 80 | 3.8435
CZ11/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ12/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 2405.97 | 9192.95 | 1787.21 | 7171.47 | 2684.72 | 9250.52 | 2377.66 | 14808.62 | 1760.98 | 13643.97 | 2677.74 | 14938.56 | 2374.74 | 14465.28 | 1754.36 | 6837.95 | 2672.04 | 9153.71 | 2674.18 | 9184 | 1759.71 | 6867.05 | 2379.95 | 14691.56 | 6563.1208 | 3646.1782 | 12.1492 | 12.4408 | 80 | 6.4305
CZ12/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ13/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6983.13 | 16546.61 | 5339.33 | 13643.67 | 7043.98 | 16572.88 | 6978.19 | 23100.79 | 5331.91 | 20644.39 | 7041.64 | 23105.85 | 6976.89 | 23436.21 | 5322.66 | 13469.4 | 7031.39 | 16504.46 | 7042.06 | 16531.94 | 5331.28 | 13489.39 | 6985.19 | 23651.85 | 12421.0454 | 6900.5808 | 22.993 | 23.5448 | 80 | 3.3978
CZ13/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ14/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4684.13 | 11101.24 | 5084.42 | 8323.43 | 4771.55 | 11158.13 | 4683.79 | 16829.37 | 5086.61 | 14958.7 | 4772.2 | 17002.8 | 4682.3 | 16712.91 | 5066.99 | 8190.65 | 4760.11 | 11490.41 | 4770.67 | 11745.46 | 5085.34 | 8215.34 | 4692.91 | 16945.86 | 8783.9717 | 4879.9843 | 16.2603 | 16.6505 | 80 | 4.8047
CZ14/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ15/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6427.1 | 15576.84 | 4902.08 | 12959.65 | 6748.46 | 15850.52 | 6419.72 | 24240.28 | 4895.27 | 21608.07 | 6740.73 | 24646 | 6416.21 | 23690.58 | 4894.75 | 12947.47 | 6747.6 | 16938.58 | 6748.33 | 17626.67 | 4895.37 | 13540.08 | 6416.64 | 24310.01 | 12341.1254 | 6856.1808 | 22.845 | 23.3933 | 80 | 3.4198
CZ15/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
CZ16/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 4078.5 | 13222.73 | 2990.4 | 11062.63 | 4213.08 | 13425.83 | 4043.4 | 23019.67 | 2962.69 | 21102.96 | 4188.07 | 23228.15 | 4040.66 | 22370.1 | 2959.47 | 10815.36 | 4211.7 | 13390.04 | 4200.87 | 13553.92 | 2956.3 | 10968.92 | 4037.78 | 22736.55 | 10157.4908 | 5643.0505 | 18.8028 | 19.2541 | 80 | 4.155
CZ16/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql
File Name
CZ01/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ01/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 656.23 | 2400.79 | 80.95 | 2224.68 | 539.06 | 1940.63 | 662.49 | 6981.88 | 84.33 | 6957.52 | 542.26 | 6967.09 | 661.52 | 7019.54 | 80.95 | 1297.29 | 533.4 | 3905.11 | 536.62 | 3960.07 | 84.33 | 1302.5 | 667.78 | 7025.66
CZ02/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ02/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1547.72 | 6267.08 | 1278.81 | 5417.09 | 1618.05 | 6307.26 | 1526.44 | 10360.65 | 1255.01 | 9663.21 | 1596.35 | 10371.55 | 1524.8 | 10356.54 | 1253.41 | 5130.45 | 1607.64 | 6201.38 | 1609.29 | 6215.36 | 1254.95 | 5139.15 | 1525.81 | 10382.22
CZ03/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ03/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1713.45 | 6843.51 | 1192.97 | 5870.15 | 1745.47 | 6320.29 | 1693.15 | 11635.9 | 1174.18 | 10943.75 | 1725.49 | 11641.59 | 1693.85 | 11405.29 | 1180.33 | 4663.97 | 1749.17 | 8324.93 | 1741.71 | 8317.7 | 1173.68 | 4650.7 | 1686.69 | 11418.42
CZ04/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ04/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1721.79 | 6456.09 | 1418.83 | 5617.15 | 1789.23 | 6546.71 | 1705.89 | 10591.73 | 1402.26 | 9841.81 | 1774.24 | 10588.34 | 1705.55 | 10597.39 | 1401.5 | 5419.9 | 1782.87 | 6492.4 | 1782.98 | 6494.03 | 1401.2 | 5420.41 | 1704.79 | 10617.74
CZ05/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ05/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1776.89 | 6324.62 | 1109.89 | 5167.35 | 1837.29 | 6287.3 | 1786.09 | 11880.27 | 1118.78 | 11290.48 | 1846.33 | 11861.82 | 1784.95 | 11561.99 | 1109.89 | 4691.24 | 1828.73 | 7379.31 | 1837.8 | 7413.53 | 1118.78 | 4684.06 | 1794.15 | 11598.3
CZ06/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ06/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1820.82 | 6692.39 | 1261.4 | 5809.14 | 1863.48 | 6254.11 | 1806.55 | 10988.56 | 1248 | 10308.05 | 1849.24 | 11008.11 | 1806.29 | 10773.37 | 1247.47 | 4630.7 | 1857.08 | 8062.86 | 1862.37 | 8116.95 | 1252.36 | 4647.01 | 1811.52 | 10814.54
CZ07/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ07/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1363.03 | 5717.09 | 1201.13 | 5292.12 | 1528.07 | 5594.07 | 1355.41 | 10803.65 | 1191.74 | 10297.98 | 1519.93 | 10819.37 | 1352.4 | 10537.7 | 1190.65 | 4897.1 | 1531.64 | 7438.82 | 1527.15 | 7545.97 | 1188.97 | 4913.65 | 1348.02 | 10613.1
CZ08/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ08/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1907.63 | 6918.61 | 1649.77 | 5988.25 | 2088.75 | 7002.2 | 1902.44 | 12850.19 | 1644.79 | 12044.38 | 2079.44 | 12923.63 | 1897.94 | 12525.42 | 1642.41 | 5864.41 | 2087.84 | 8294.63 | 2087.07 | 8376.62 | 1642.25 | 5995.13 | 1896.55 | 12651.35
CZ09/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ09/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2096.01 | 7981.85 | 1674.58 | 6909.83 | 2214.05 | 8056.79 | 2089.75 | 14022.2 | 1666.27 | 13072.38 | 2207.11 | 14027.27 | 2087.14 | 13845.4 | 1664.9 | 6813.76 | 2211.82 | 9664.96 | 2212.03 | 9760.02 | 1665.09 | 6815.88 | 2087.2 | 13875.36
CZ10/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ10/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2682.15 | 7514.35 | 1861.09 | 5848.99 | 2730.73 | 7527.12 | 2670.12 | 12325.52 | 1848.52 | 11299.19 | 2718.78 | 12367.71 | 2667.84 | 12012.7 | 1846.48 | 5561.66 | 2724.29 | 7439.87 | 2724.6 | 7448.25 | 1846.83 | 5705.93 | 2668.09 | 12055.43
CZ11/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ11/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3312.09 | 9312.46 | 2515.64 | 7927.33 | 3509.45 | 9582.69 | 3299.55 | 14932.15 | 2538.25 | 13389.7 | 3498.58 | 14957.5 | 3302.51 | 14555.65 | 2506.18 | 7885.68 | 3507.15 | 9957.92 | 3503.87 | 10233.95 | 2502.97 | 7883.19 | 3299.5 | 14597.78
CZ12/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ12/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 1584.65 | 6168.3 | 1196.78 | 4809.45 | 1789.6 | 6209.56 | 1566.05 | 9936.3 | 1179.22 | 9150.11 | 1784.89 | 10027.72 | 1564.01 | 9705.92 | 1174.79 | 4585.78 | 1781.15 | 6144.57 | 1782.58 | 6164.91 | 1178.36 | 4605.29 | 1567.45 | 9857.75
CZ13/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ13/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4832.42 | 11450.35 | 3694.95 | 9441.6 | 4874.52 | 11468.54 | 4829 | 15985.88 | 3689.82 | 14286.18 | 4872.9 | 15989.39 | 4828.1 | 16218 | 3683.42 | 9320.99 | 4865.81 | 11421.19 | 4873.19 | 11440.21 | 3689.38 | 9334.83 | 4833.84 | 16367.22
CZ14/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ14/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 3436.67 | 8144.63 | 2238.34 | 6106.67 | 3500.7 | 8186.33 | 3436.42 | 12347.18 | 2239.3 | 10974.78 | 3501.18 | 12474.36 | 3435.33 | 12261.73 | 2230.67 | 6009.25 | 3492.32 | 8430.12 | 3500.06 | 8617.24 | 2238.75 | 6027.37 | 3443.12 | 12432.64
CZ15/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ15/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4472.57 | 10839.76 | 3411.36 | 9018.52 | 4696.2 | 11030.19 | 4467.43 | 16868.55 | 3406.63 | 15036.87 | 4690.82 | 17150.86 | 4464.99 | 16486.03 | 3406.26 | 9010.03 | 4695.6 | 11787.36 | 4696.11 | 12266.19 | 3406.7 | 9422.43 | 4465.29 | 16917.08
CZ16/MFm&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql
CZ16/MFm&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 2971.65 | 9634.12 | 2178.89 | 8060.33 | 3069.69 | 9782.11 | 2946.08 | 16772.2 | 2158.7 | 15375.8 | 3051.47 | 16924.11 | 2944.08 | 16298.92 | 2156.35 | 7880.17 | 3068.69 | 9756.03 | 3060.79 | 9875.44 | 2154.04 | 7992.05 | 2941.98 | 16565.92

## results-summary_DMo
File Name | Conditioned Area (m2) | Conditioned Area (ft2)
CZ01/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ01/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ02/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ02/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ03/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ03/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ04/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ04/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ05/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ05/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ06/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ06/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ07/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ07/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ08/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ08/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ09/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ09/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ10/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ10/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ11/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ11/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ12/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ12/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ13/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ13/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ14/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ14/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ15/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ15/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
CZ16/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 230.77 | 1241.9926
CZ16/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 230.77 | 1241.9926
Sizing Factor Removed
| The model uses 1.8 sizing factor |  |  |  | Air Conditioner |  |  |  | Heat Pump |  |  | Furnace from below for comparison
File Name | DX Coil Cool Capacity (W) | DX Coil Cool Capacity (W) | Average of two orientations (W) | 1.8 sizing factor removed (W) | Model AC SFm SF/ton cool capacity | Model DX Coil Cool Capacity (tons) | AC Suggested Sizing (Tons) | Sizing Factor (dimensionless multiplier on design loads) | Model HP capacity (kBtu/hr) | Heat Pump Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads) | Model Fuel Coil Heat Capacity (kBtu/hr) | Furnace Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads)
CZ01/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 3087.98 | 3871.74 | 3479.86 | 1933.2556 | 2259.446 | 0.54969 | 3.5 | 6.3672 |  |  |  | 17.1129 | 80 | 4.6748
CZ01/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4632.36 | 5808.09 | 5220.225 | 2900.125 | 1506.1718 | 0.8246 | 3.5 | 4.2445 | 9.8952 | 39.9 | 4.0322
CZ02/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7161.67 | 7229.08 | 7195.375 | 3997.4306 | 1092.7236 | 1.1366 | 3.5 | 3.0794 |  |  |  | 27.8504 | 80 | 2.8725
CZ02/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9332.78 | 9546.14 | 9439.46 | 5244.1444 | 832.9455 | 1.4911 | 3.5 | 2.3473 | 17.893 | 39.9 | 2.2299
CZ03/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7376.63 | 7223.3 | 7299.965 | 4055.5361 | 1077.0676 | 1.1531 | 2.5 | 2.168 |  |  |  | 31.9379 | 80 | 2.5049
CZ03/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 11065.86 | 10835.85 | 10950.855 | 6083.8083 | 717.9856 | 1.7298 | 2.5 | 1.4452 | 20.758 | 28.5 | 1.373
CZ04/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6883.96 | 7254.09 | 7069.025 | 3927.2361 | 1112.2546 | 1.1166 | 3.5 | 3.1344 |  |  |  | 27.7111 | 80 | 2.8869
CZ04/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9155.59 | 9822.63 | 9489.11 | 5271.7278 | 828.5873 | 1.4989 | 3.5 | 2.335 | 17.9871 | 39.9 | 2.2183
CZ05/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7396.39 | 7450.72 | 7423.555 | 4124.1972 | 1059.1362 | 1.1726 | 3 | 2.5583 |  |  |  | 32.3024 | 80 | 2.4766
CZ05/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 11095.5 | 11177 | 11136.25 | 6186.8056 | 706.0326 | 1.7591 | 3 | 1.7054 | 21.1094 | 34.2 | 1.6201
CZ06/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 6265.42 | 6944.65 | 6605.035 | 3669.4639 | 1190.3882 | 1.0434 | 3 | 2.8754 |  |  |  | 30.1517 | 80 | 2.6532
CZ06/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9398.9 | 10417.84 | 9908.37 | 5504.65 | 793.5267 | 1.5652 | 3 | 1.9167 | 18.7819 | 34.2 | 1.8209
CZ07/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7442.87 | 8134.01 | 7788.44 | 4326.9111 | 1009.5161 | 1.2303 | 2.5 | 2.032 |  |  |  | 36.6402 | 80 | 2.1834
CZ07/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 10865.48 | 12186.28 | 11525.88 | 6403.2667 | 682.1653 | 1.8207 | 2.5 | 1.3731 | 21.8479 | 28.5 | 1.3045
CZ08/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 7332.63 | 8287.91 | 7810.27 | 4339.0389 | 1006.6945 | 1.2337 | 2.5 | 2.0264 |  |  |  | 34.2535 | 80 | 2.3355
CZ08/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 10247.83 | 11312.35 | 10780.09 | 5988.9389 | 729.359 | 1.7029 | 2.5 | 1.4681 | 20.4343 | 28.5 | 1.3947
CZ09/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 9606.88 | 10470.07 | 10038.475 | 5576.9306 | 783.2421 | 1.5857 | 2.5 | 1.5766 |  |  |  | 39.968 | 80 | 2.0016
CZ09/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 14160.4 | 14765.96 | 14463.18 | 8035.1 | 543.6257 | 2.2846 | 2.5 | 1.0943 | 27.4158 | 28.5 | 1.0395
CZ10/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 8280.76 | 8251.35 | 8266.055 | 4592.2528 | 951.186 | 1.3057 | 3 | 2.2976 |  |  |  | 27.2305 | 80 | 2.9379
CZ10/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 10049.53 | 10191.22 | 10120.375 | 5622.4306 | 776.9036 | 1.5986 | 3 | 1.8766 | 19.1837 | 34.2 | 1.7828
CZ11/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 10988.5 | 11395.38 | 11191.94 | 6217.7444 | 702.5195 | 1.7679 | 4 | 2.2626 |  |  |  | 39.7683 | 80 | 2.0117
CZ11/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 13768.61 | 15210.7 | 14489.655 | 8049.8083 | 542.6324 | 2.2888 | 4 | 1.7476 | 27.4659 | 45.6 | 1.6602
CZ12/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 9587 | 9080.16 | 9333.58 | 5185.3222 | 842.3944 | 1.4744 | 3.5 | 2.3739 |  |  |  | 32.9982 | 80 | 2.4244
CZ12/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 12021.59 | 11812.55 | 11917.07 | 6620.5944 | 659.7726 | 1.8825 | 3.5 | 1.8593 | 22.5895 | 39.9 | 1.7663
CZ13/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 10318.7 | 10765.94 | 10542.32 | 5856.8444 | 745.8089 | 1.6653 | 4 | 2.402 |  |  |  | 37.0948 | 80 | 2.1566
CZ13/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 12886.3 | 14197.62 | 13541.96 | 7523.3111 | 580.6069 | 2.1391 | 4 | 1.8699 | 25.6695 | 45.6 | 1.7764
CZ14/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 10072.09 | 9908.18 | 9990.135 | 5550.075 | 787.032 | 1.5781 | 5 | 3.1684 |  |  |  | 28.2325 | 80 | 2.8336
CZ14/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 11872.81 | 11967.63 | 11920.22 | 6622.3444 | 659.5982 | 1.883 | 5 | 2.6554 | 22.5954 | 57 | 2.5226
CZ15/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 13075.12 | 13412.07 | 13243.595 | 7357.5528 | 593.6874 | 2.092 | 5 | 2.3901 |  |  |  | 42.7723 | 80 | 1.8704
CZ15/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 15362.88 | 16586.93 | 15974.905 | 8874.9472 | 492.1817 | 2.5234 | 5 | 1.9814 | 30.2813 | 57 | 1.8823
CZ16/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 9555.88 | 10469.87 | 10012.875 | 5562.7083 | 785.2446 | 1.5817 | 3.5 | 2.2129 |  |  |  | 41.5742 | 80 | 1.9243
CZ16/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 13757.97 | 15706.1 | 14732.035 | 8184.4639 | 533.7047 | 2.3271 | 3.5 | 1.504 | 27.9254 | 39.9 | 1.4288
File Name | Fuel Coil Heat Capacity (W) | Fuel Coil Heat Capacity (W) | Average of two orientations (W) | 1.8 sizing factor removed (W) | Model Gas Furnace SFm Btu/hr-SF | Model Fuel Coil Heat Capacity (kBtu/hr) | Furnace Suggested Sizing (kBtu/hr) | Sizing Factor (dimensionless multiplier on design loads)
CZ01/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 8011.25 | 10044.57 | 9027.91 | 5015.5056 | 13.7785 | 17.1129 | 80 | 4.6748
CZ02/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 14526.44 | 14858.53 | 14692.485 | 8162.4917 | 22.4238 | 27.8504 | 80 | 2.8725
CZ03/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 17025.77 | 16671.88 | 16848.825 | 9360.4583 | 25.7149 | 31.9379 | 80 | 2.5049
CZ04/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 14105.15 | 15132.8 | 14618.975 | 8121.6528 | 22.3117 | 27.7111 | 80 | 2.8869
CZ05/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 16978.78 | 17103.49 | 17041.135 | 9467.2972 | 26.0084 | 32.3024 | 80 | 2.4766
CZ06/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 15088.66 | 16724.43 | 15906.545 | 8836.9694 | 24.2768 | 30.1517 | 80 | 2.6532
CZ07/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 18221.99 | 20437.04 | 19329.515 | 10738.6194 | 29.5009 | 36.6402 | 80 | 2.1834
CZ08/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 17178.2 | 18962.63 | 18070.415 | 10039.1194 | 27.5793 | 34.2535 | 80 | 2.3355
CZ09/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 20643.75 | 21526.52 | 21085.135 | 11713.9639 | 32.1804 | 39.968 | 80 | 2.0016
CZ10/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 14264.91 | 14466.03 | 14365.47 | 7980.8167 | 21.9248 | 27.2305 | 80 | 2.9379
CZ11/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 19935.74 | 22023.75 | 20979.745 | 11655.4139 | 32.0195 | 39.7683 | 80 | 2.0117
CZ12/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 17560.89 | 17255.53 | 17408.21 | 9671.2278 | 26.5686 | 32.9982 | 80 | 2.4244
CZ13/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 18621.89 | 20516.86 | 19569.375 | 10871.875 | 29.867 | 37.0948 | 80 | 2.1566
CZ14/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 14834.82 | 14953.3 | 14894.06 | 8274.4778 | 22.7315 | 28.2325 | 80 | 2.8336
CZ15/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 21700.01 | 23428.99 | 22564.5 | 12535.8333 | 34.4382 | 42.7723 | 80 | 1.8704
CZ16/DMo&0&rDXGF&Ex&dxAC_equip/dxAC-Res-SEER-13.0/instance-out.sql | 20482.33 | 23382.64 | 21932.485 | 12184.7139 | 33.4736 | 41.5742 | 80 | 1.9243
File Name | Elec Coil Heat Capacity (W) | Elec Coil Heat Capacity (W) | Average | Elec Coil Heat Capacity (Btu/hr)
CZ01/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 4632.36 | 5808.09 | 5220.225 | 17800.9673
CZ02/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9332.78 | 9546.14 | 9439.46 | 32188.5586
CZ03/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 11065.86 | 10835.85 | 10950.855 | 37342.4155
CZ04/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9155.59 | 9822.63 | 9489.11 | 32357.8651
CZ05/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 11095.5 | 11177 | 11136.25 | 37974.6125
CZ06/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 9398.9 | 10417.84 | 9908.37 | 33787.5417
CZ07/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 10865.48 | 12186.28 | 11525.88 | 39303.2508
CZ08/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 10247.83 | 11312.35 | 10780.09 | 36760.1069
CZ09/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 14160.4 | 14765.96 | 14463.18 | 49319.4438
CZ10/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 10049.53 | 10191.22 | 10120.375 | 34510.4788
CZ11/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 13768.61 | 15210.7 | 14489.655 | 49409.7236
CZ12/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 12021.59 | 11812.55 | 11917.07 | 40637.2087
CZ13/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 12886.3 | 14197.62 | 13541.96 | 46178.0836
CZ14/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 11872.81 | 11967.63 | 11920.22 | 40647.9502
CZ15/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 15362.88 | 16586.93 | 15974.905 | 54474.4261
CZ16/DMo&0&rDXHP&Ex&dxHP_equip/HSPF_7p0_SEER_13_Pre/instance-out.sql | 13757.97 | 15706.1 | 14732.035 | 50236.2394

## SFm DMo and MFm sizing results
SWHC049-03 SEER Rated AC HP_SFm_1985 | SFm&2&rDXHP&Ex&dxHP_equip | HSPF_7p0_SEER_13_Pre
See row 8088 for comparison to DNV outputs
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL2 | Cooling | Sensible | 7196.2 | 0.55284 | 0.55284 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL2 | Heating | Sensible | 8677.23 | 0.20205 | 0.20205 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ01 | 3 | DXGF EL5 | Cooling | Sensible | 5320.16 | 0.40871 | 0.40871 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL5 | Heating | Sensible | 8663.76 | 0.20174 | 0.20174 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ02 | 1 | DXGF EL2 | Cooling | Sensible | 13789.8 | 0.77016 | 0.77016 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL2 | Heating | Sensible | 10370.62 | 0.26831 | 0.26831 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 16:00
CZ02 | 3 | DXGF EL5 | Cooling | Sensible | 11933.75 | 0.66183 | 0.66183 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL5 | Heating | Sensible | 10360.86 | 0.26806 | 0.26806 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 16:00
CZ03 | 1 | DXGF EL2 | Cooling | Sensible | 13269.78 | 0.92511 | 0.92511 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL2 | Heating | Sensible | 9883.22 | 0.25868 | 0.25868 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL5 | Cooling | Sensible | 11063.63 | 0.77131 | 0.77131 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL5 | Heating | Sensible | 9882.47 | 0.25866 | 0.25866 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL2 | Cooling | Sensible | 14479.7 | 0.82604 | 0.82604 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL2 | Heating | Sensible | 10454.38 | 0.27327 | 0.27327 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL5 | Cooling | Sensible | 12281.48 | 0.68067 | 0.68067 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL5 | Heating | Sensible | 10439.09 | 0.27287 | 0.27287 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL2 | Cooling | Sensible | 13783.36 | 0.96612 | 0.96612 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL2 | Heating | Sensible | 11369.36 | 0.2992 | 0.2992 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 3 | DXGF EL5 | Cooling | Sensible | 11235.85 | 0.78755 | 0.78755 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL5 | Heating | Sensible | 11368.47 | 0.29917 | 0.29917 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 1 | DXGF EL2 | Cooling | Sensible | 13043.33 | 0.87666 | 0.87666 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL2 | Heating | Sensible | 5633 | 0.1413 | 0.1413 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL5 | Cooling | Sensible | 10674.74 | 0.71746 | 0.71746 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL5 | Heating | Sensible | 5623.86 | 0.14107 | 0.14107 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL2 | Cooling | Sensible | 13895.46 | 0.8774 | 0.8774 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL2 | Heating | Sensible | 4720.23 | 0.11334 | 0.11334 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXGF EL5 | Cooling | Sensible | 11227.81 | 0.70154 | 0.70154 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL5 | Heating | Sensible | 4714.1 | 0.1132 | 0.1132 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXGF EL2 | Cooling | Sensible | 14450.33 | 0.8109 | 0.8109 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL2 | Heating | Sensible | 5536.74 | 0.13301 | 0.13301 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 3 | DXGF EL5 | Cooling | Sensible | 11361.19 | 0.61734 | 0.61734 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL5 | Heating | Sensible | 5526.83 | 0.13277 | 0.13277 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXGF EL2 | Cooling | Sensible | 18069.22 | 1.142 | 1.142 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL2 | Heating | Sensible | 11717.98 | 0.32383 | 0.32383 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL5 | Cooling | Sensible | 14401.93 | 0.95817 | 0.95817 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL5 | Heating | Sensible | 11713.01 | 0.32369 | 0.32369 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL2 | Cooling | Sensible | 13855.86 | 0.76859 | 0.76859 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL2 | Heating | Sensible | 8453.96 | 0.23984 | 0.23984 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL5 | Cooling | Sensible | 11529.8 | 0.64264 | 0.64264 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL5 | Heating | Sensible | 8434.43 | 0.23928 | 0.23928 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL2 | Cooling | Sensible | 16147.55 | 0.94307 | 0.94307 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL2 | Heating | Sensible | 12430.2 | 0.34555 | 0.34555 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL5 | Cooling | Sensible | 12743.9 | 0.73374 | 0.73374 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL5 | Heating | Sensible | 12409.07 | 0.34497 | 0.34497 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL2 | Cooling | Sensible | 14261.33 | 0.81597 | 0.81597 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL2 | Heating | Sensible | 10515.94 | 0.2899 | 0.2899 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL5 | Cooling | Sensible | 10846.86 | 0.60928 | 0.60928 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL5 | Heating | Sensible | 10484.75 | 0.28904 | 0.28904 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL2 | Cooling | Sensible | 17487.7 | 1.006 | 1.006 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL2 | Heating | Sensible | 10665.66 | 0.29722 | 0.29722 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL5 | Cooling | Sensible | 13171.17 | 0.76595 | 0.76595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL5 | Heating | Sensible | 10640.14 | 0.2965 | 0.2965 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL2 | Cooling | Sensible | 16355.95 | 0.91876 | 0.91876 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL2 | Heating | Sensible | 9823.84 | 0.31661 | 0.31661 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL5 | Cooling | Sensible | 12213.31 | 0.68606 | 0.68606 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL5 | Heating | Sensible | 9792.05 | 0.31559 | 0.31559 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL2 | Cooling | Sensible | 18766.46 | 1.0581 | 1.0581 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL2 | Heating | Sensible | 9606.2 | 0.27377 | 0.27377 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL5 | Cooling | Sensible | 15178.79 | 0.8956 | 0.8956 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL5 | Heating | Sensible | 9580.78 | 0.27305 | 0.27305 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL2 | Cooling | Sensible | 13775.5 | 0.92179 | 0.92179 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL2 | Heating | Sensible | 10569.77 | 0.2859 | 0.2859 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL5 | Cooling | Sensible | 9976.87 | 0.6982 | 0.6982 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL5 | Heating | Sensible | 10540.73 | 0.28512 | 0.28512 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 13596.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 10181.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 18727.8 | 18727.8 | 6.72 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 14024.6 | 14024.6 | 6.8 | 4
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18368.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15784.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 25300.9 | 25300.9 | 6.8 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 21742.3 | 21742.3 | 6.72 | 4
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 22064.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 18395.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30391.3 | 30391.3 | 6.74 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25338.6 | 25338.6 | 6.8 | 4
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 19701.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16234.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 27136.6 | 27136.6 | 6.74 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 22361.2 | 22361.2 | 6.81 | 4
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 23042.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 18783.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 31738.4 | 31738.4 | 6.78 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25872.3 | 25872.3 | 6.78 | 4
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 20908.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 17111.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 28799.6 | 28799.6 | 6.78 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 23569.8 | 23569.8 | 6.76 | 4
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 20926.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16732 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 28824.1 | 28824.1 | 6.78 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 23046.8 | 23046.8 | 6.78 | 4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 19340.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14723.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 26639.3 | 26639.3 | 6.76 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 20280.4 | 20280.4 | 6.78 | 4
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 27236.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 22852.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 37515.8 | 37515.8 | 6.78 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 31477.4 | 31477.4 | 6.79 | 4
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18331.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15327.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 25249.4 | 25249.4 | 6.8 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 21111.9 | 21111.9 | 6.74 | 4
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 22492.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 17499.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30981.2 | 30981.2 | 6.8 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 24104.5 | 24104.5 | 6.75 | 4
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 19461 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14531.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 26805.8 | 26805.8 | 6.75 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 20015.7 | 20015.7 | 6.79 | 4
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 23992.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 18268.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 33047.3 | 33047.3 | 6.75 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25162.7 | 25162.7 | 6.81 | 4
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 21912.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16362.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30182.8 | 30182.8 | 6.74 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 22538 | 22538 | 6.8 | 4
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 25235.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 21360.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 34759.2 | 34759.2 | 6.71 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 29422 | 29422 | 6.76 | 4
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 21985 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16652.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30282.4 | 30282.4 | 6.74 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 22937.1 | 22937.1 | 6.79 | 4
DX Heating Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 18727.8 | 18727.8 | 6.72 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 14024.6 | 14024.6 | 6.8 | 4
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 25300.9 | 25300.9 | 6.8 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 21742.3 | 21742.3 | 6.72 | 4
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30391.3 | 30391.3 | 6.74 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25338.6 | 25338.6 | 6.8 | 4
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 27136.6 | 27136.6 | 6.74 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 22361.2 | 22361.2 | 6.81 | 4
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 31738.4 | 31738.4 | 6.78 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25872.3 | 25872.3 | 6.78 | 4
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 28799.6 | 28799.6 | 6.78 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 23569.8 | 23569.8 | 6.76 | 4
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 28824.1 | 28824.1 | 6.78 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 23046.8 | 23046.8 | 6.78 | 4
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 26639.3 | 26639.3 | 6.76 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 20280.4 | 20280.4 | 6.78 | 4
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 37515.8 | 37515.8 | 6.78 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 31477.4 | 31477.4 | 6.79 | 4
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 25249.4 | 25249.4 | 6.8 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 21111.9 | 21111.9 | 6.74 | 4
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30981.2 | 30981.2 | 6.8 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 24104.5 | 24104.5 | 6.75 | 4
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 26805.8 | 26805.8 | 6.75 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 20015.7 | 20015.7 | 6.79 | 4
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 33047.3 | 33047.3 | 6.75 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25162.7 | 25162.7 | 6.81 | 4
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30182.8 | 30182.8 | 6.74 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 22538 | 22538 | 6.8 | 4
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 34759.2 | 34759.2 | 6.71 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 29422 | 29422 | 6.76 | 4
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30282.4 | 30282.4 | 6.74 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 22937.1 | 22937.1 | 6.79 | 4
SWHC049-03 SEER Rated AC HP_SFm_1985 | SFm&2&rDXGF&Ex&dxAC_equip | dxAC-Res-SEER-13.0
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL2 | Cooling | Sensible | 7196.2 | 0.55284 | 0.55284 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL2 | Heating | Sensible | 8677.23 | 0.20205 | 0.20205 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ01 | 3 | DXGF EL5 | Cooling | Sensible | 5320.16 | 0.40871 | 0.40871 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL5 | Heating | Sensible | 8663.76 | 0.20174 | 0.20174 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ02 | 1 | DXGF EL2 | Cooling | Sensible | 13789.8 | 0.77016 | 0.77016 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL2 | Heating | Sensible | 10370.62 | 0.26831 | 0.26831 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 16:00
CZ02 | 3 | DXGF EL5 | Cooling | Sensible | 11933.75 | 0.66183 | 0.66183 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL5 | Heating | Sensible | 10360.86 | 0.26806 | 0.26806 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 16:00
CZ03 | 1 | DXGF EL2 | Cooling | Sensible | 13269.78 | 0.92511 | 0.92511 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL2 | Heating | Sensible | 9883.22 | 0.25868 | 0.25868 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL5 | Cooling | Sensible | 11063.63 | 0.77131 | 0.77131 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL5 | Heating | Sensible | 9882.47 | 0.25866 | 0.25866 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL2 | Cooling | Sensible | 14479.7 | 0.82604 | 0.82604 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL2 | Heating | Sensible | 10454.38 | 0.27327 | 0.27327 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL5 | Cooling | Sensible | 12281.48 | 0.68067 | 0.68067 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL5 | Heating | Sensible | 10439.09 | 0.27287 | 0.27287 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL2 | Cooling | Sensible | 13783.36 | 0.96612 | 0.96612 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL2 | Heating | Sensible | 11369.36 | 0.2992 | 0.2992 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 3 | DXGF EL5 | Cooling | Sensible | 11235.85 | 0.78755 | 0.78755 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL5 | Heating | Sensible | 11368.47 | 0.29917 | 0.29917 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 1 | DXGF EL2 | Cooling | Sensible | 13043.33 | 0.87666 | 0.87666 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL2 | Heating | Sensible | 5633 | 0.1413 | 0.1413 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL5 | Cooling | Sensible | 10674.74 | 0.71746 | 0.71746 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL5 | Heating | Sensible | 5623.86 | 0.14107 | 0.14107 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL2 | Cooling | Sensible | 13895.46 | 0.8774 | 0.8774 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL2 | Heating | Sensible | 4720.23 | 0.11334 | 0.11334 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXGF EL5 | Cooling | Sensible | 11227.81 | 0.70154 | 0.70154 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL5 | Heating | Sensible | 4714.1 | 0.1132 | 0.1132 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXGF EL2 | Cooling | Sensible | 14450.33 | 0.8109 | 0.8109 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL2 | Heating | Sensible | 5536.74 | 0.13301 | 0.13301 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 3 | DXGF EL5 | Cooling | Sensible | 11361.19 | 0.61734 | 0.61734 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL5 | Heating | Sensible | 5526.83 | 0.13277 | 0.13277 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXGF EL2 | Cooling | Sensible | 18069.22 | 1.142 | 1.142 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL2 | Heating | Sensible | 11717.98 | 0.32383 | 0.32383 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL5 | Cooling | Sensible | 14401.93 | 0.95817 | 0.95817 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL5 | Heating | Sensible | 11713.01 | 0.32369 | 0.32369 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL2 | Cooling | Sensible | 13855.86 | 0.76859 | 0.76859 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL2 | Heating | Sensible | 8453.96 | 0.23984 | 0.23984 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL5 | Cooling | Sensible | 11529.8 | 0.64264 | 0.64264 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL5 | Heating | Sensible | 8434.43 | 0.23928 | 0.23928 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL2 | Cooling | Sensible | 16147.55 | 0.94307 | 0.94307 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL2 | Heating | Sensible | 12430.2 | 0.34555 | 0.34555 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL5 | Cooling | Sensible | 12743.9 | 0.73374 | 0.73374 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL5 | Heating | Sensible | 12409.07 | 0.34497 | 0.34497 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL2 | Cooling | Sensible | 14261.33 | 0.81597 | 0.81597 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL2 | Heating | Sensible | 10515.94 | 0.2899 | 0.2899 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL5 | Cooling | Sensible | 10846.86 | 0.60928 | 0.60928 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL5 | Heating | Sensible | 10484.75 | 0.28904 | 0.28904 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL2 | Cooling | Sensible | 17487.7 | 1.006 | 1.006 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL2 | Heating | Sensible | 10665.66 | 0.29722 | 0.29722 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL5 | Cooling | Sensible | 13171.17 | 0.76595 | 0.76595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL5 | Heating | Sensible | 10640.14 | 0.2965 | 0.2965 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL2 | Cooling | Sensible | 16355.95 | 0.91876 | 0.91876 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL2 | Heating | Sensible | 9823.84 | 0.31661 | 0.31661 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL5 | Cooling | Sensible | 12213.31 | 0.68606 | 0.68606 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL5 | Heating | Sensible | 9792.05 | 0.31559 | 0.31559 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL2 | Cooling | Sensible | 18766.46 | 1.0581 | 1.0581 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL2 | Heating | Sensible | 9606.2 | 0.27377 | 0.27377 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL5 | Cooling | Sensible | 15178.79 | 0.8956 | 0.8956 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL5 | Heating | Sensible | 9580.78 | 0.27305 | 0.27305 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL2 | Cooling | Sensible | 13775.5 | 0.92179 | 0.92179 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL2 | Heating | Sensible | 10569.77 | 0.2859 | 0.2859 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL5 | Cooling | Sensible | 9976.87 | 0.6982 | 0.6982 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL5 | Heating | Sensible | 10540.73 | 0.28512 | 0.28512 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 8916.5 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 6677.3 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 14171.2 | 2.72 | 9.27 | 10.49 | 9.93 | 10.3
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12270.8 | 2.72 | 9.28 | 10.51 | 9.94 | 10.32
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 14469.7 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12064 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 14902.2 | 2.71 | 9.24 | 10.46 | 9.89 | 10.25
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12667.9 | 2.72 | 9.28 | 10.51 | 9.94 | 10.33
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15111 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12318.1 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 13711.8 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 11221.9 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 14435 | 2.67 | 9.11 | 10.29 | 9.74 | 10.01
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 11730.7 | 2.68 | 9.13 | 10.32 | 9.77 | 10.05
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15059 | 2.72 | 9.28 | 10.51 | 9.94 | 10.33
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 11855.5 | 2.73 | 9.33 | 10.56 | 9.99 | 10.41
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18814.2 | 2.67 | 9.11 | 10.3 | 9.74 | 10.01
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15054 | 2.65 | 9.04 | 10.21 | 9.66 | 9.88
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15210.2 | 2.74 | 9.37 | 10.61 | 10.04 | 10.49
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12815.3 | 2.75 | 9.38 | 10.63 | 10.05 | 10.51
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 17757.8 | 2.73 | 9.3 | 10.53 | 9.96 | 10.36
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14107.1 | 2.73 | 9.33 | 10.57 | 10 | 10.42
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15628.4 | 2.73 | 9.32 | 10.56 | 9.99 | 10.41
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12004.7 | 2.74 | 9.36 | 10.61 | 10.03 | 10.48
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 19478.8 | 2.74 | 9.34 | 10.58 | 10.01 | 10.43
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14767.2 | 2.73 | 9.33 | 10.57 | 10 | 10.42
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18415.4 | 2.75 | 9.38 | 10.63 | 10.06 | 10.52
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 13956.8 | 2.76 | 9.4 | 10.66 | 10.08 | 10.56
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 21540.8 | 2.76 | 9.4 | 10.66 | 10.08 | 10.56
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 17319.9 | 2.74 | 9.34 | 10.58 | 10 | 10.43
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15105.4 | 2.67 | 9.1 | 10.29 | 9.73 | 10
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 10920.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
SWHC049-03 SEER Rated AC HP_SFm_1985 | SFm&1&rDXHP&Ex&dxHP_equip | HSPF_7p0_SEER_13_Pre
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXGF EL7 | Heating | Sensible | 3139.45 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ01 | 3 | DXGF EL8 | Cooling | Sensible | 245.72 | 0.0189 | 0.0189 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL8 | Heating | Sensible | 3137.92 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ02 | 1 | DXGF EL7 | Cooling | Sensible | 2298.09 | 0.12931 | 0.12931 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL7 | Heating | Sensible | 2919.78 | 0.0755 | 0.0755 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 45313
CZ02 | 3 | DXGF EL8 | Cooling | Sensible | 2645.89 | 0.14887 | 0.14887 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL8 | Heating | Sensible | 2915.19 | 0.0754 | 0.0754 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 45313
CZ03 | 1 | DXGF EL7 | Cooling | Sensible | 1951.09 | 0.13602 | 0.13602 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL7 | Heating | Sensible | 3794.26 | 0.0993 | 0.0993 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL8 | Cooling | Sensible | 2254.8 | 0.1572 | 0.1572 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL8 | Heating | Sensible | 3791.65 | 0.0992 | 0.0992 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL7 | Cooling | Sensible | 2795.59 | 0.15925 | 0.15925 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL7 | Heating | Sensible | 4065.06 | 0.10626 | 0.10626 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL8 | Cooling | Sensible | 3343.38 | 0.1927 | 0.1927 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL8 | Heating | Sensible | 4063.31 | 0.10621 | 0.10621 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL7 | Cooling | Sensible | 2008.9 | 0.14081 | 0.14081 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL7 | Heating | Sensible | 4371.25 | 0.11504 | 0.11504 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ05 | 3 | DXGF EL8 | Cooling | Sensible | 2373.55 | 0.16637 | 0.16637 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL8 | Heating | Sensible | 4368.22 | 0.11496 | 0.11496 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ06 | 1 | DXGF EL7 | Cooling | Sensible | 2348.21 | 0.15783 | 0.15783 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL7 | Heating | Sensible | 1784.48 | 0.0448 | 0.0448 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL8 | Cooling | Sensible | 2789 | 0.18745 | 0.18745 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL8 | Heating | Sensible | 1783.75 | 0.0447 | 0.0447 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL7 | Cooling | Sensible | 2967.58 | 0.19667 | 0.19667 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL7 | Heating | Sensible | 1214.97 | 0.0292 | 0.0292 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ07 | 3 | DXGF EL8 | Cooling | Sensible | 3557.32 | 0.23355 | 0.23355 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL8 | Heating | Sensible | 1213.67 | 0.0291 | 0.0291 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ08 | 1 | DXGF EL7 | Cooling | Sensible | 3069.23 | 0.19476 | 0.19476 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL7 | Heating | Sensible | 1660.53 | 0.0399 | 0.0399 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ08 | 3 | DXGF EL8 | Cooling | Sensible | 3490.4 | 0.2128 | 0.2128 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL8 | Heating | Sensible | 1659.73 | 0.0399 | 0.0399 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ09 | 1 | DXGF EL7 | Cooling | Sensible | 4438.4 | 0.29561 | 0.29561 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL7 | Heating | Sensible | 4846.73 | 0.13379 | 0.13379 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL8 | Cooling | Sensible | 4823 | 0.30988 | 0.30988 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL8 | Heating | Sensible | 4846.64 | 0.13379 | 0.13379 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL7 | Cooling | Sensible | 2750.25 | 0.15331 | 0.15331 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL7 | Heating | Sensible | 3308.71 | 0.0939 | 0.0939 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL8 | Cooling | Sensible | 3158.56 | 0.17641 | 0.17641 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL8 | Heating | Sensible | 3307.65 | 0.0938 | 0.0938 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL7 | Cooling | Sensible | 3623.66 | 0.21231 | 0.21231 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL7 | Heating | Sensible | 4997.83 | 0.13879 | 0.13879 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL8 | Cooling | Sensible | 4239.99 | 0.2489 | 0.2489 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL8 | Heating | Sensible | 4996.37 | 0.13875 | 0.13875 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL7 | Cooling | Sensible | 2808.12 | 0.16207 | 0.16207 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL7 | Heating | Sensible | 4574.79 | 0.12612 | 0.12612 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL8 | Cooling | Sensible | 3399.36 | 0.19654 | 0.19654 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL8 | Heating | Sensible | 4568.38 | 0.12594 | 0.12594 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL7 | Cooling | Sensible | 3872.04 | 0.22277 | 0.22277 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL7 | Heating | Sensible | 4369.72 | 0.12177 | 0.12177 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL8 | Cooling | Sensible | 4555.7 | 0.26613 | 0.26613 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL8 | Heating | Sensible | 4368.47 | 0.12174 | 0.12174 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL7 | Cooling | Sensible | 3733.5 | 0.20972 | 0.20972 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL7 | Heating | Sensible | 2487.89 | 0.0802 | 0.0802 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL8 | Cooling | Sensible | 4246.74 | 0.23855 | 0.23855 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL8 | Heating | Sensible | 2486.17 | 0.0801 | 0.0801 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL7 | Cooling | Sensible | 4943.05 | 0.28061 | 0.28061 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL7 | Heating | Sensible | 3487.47 | 0.0995 | 0.0995 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL8 | Cooling | Sensible | 5582.92 | 0.32044 | 0.32044 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL8 | Heating | Sensible | 3483.87 | 0.0994 | 0.0994 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL7 | Cooling | Sensible | 2325.75 | 0.15727 | 0.15727 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL7 | Heating | Sensible | 4159.68 | 0.11252 | 0.11252 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXGF EL8 | Cooling | Sensible | 2983.35 | 0.20069 | 0.20069 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL8 | Heating | Sensible | 4160.68 | 0.11255 | 0.11255 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 1743.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 1742.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 2401.6 | 2401.6 | 6.94 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 2400.4 | 2400.4 | 6.94 | 4
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3084 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3550.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4247.9 | 4247.9 | 6.8 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 4890.8 | 4890.8 | 6.69 | 4
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3244.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3749.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4468.5 | 4468.5 | 6.75 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 5164.1 | 5164.1 | 6.88 | 4
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3798.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4596 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5231.5 | 5231.5 | 6.86 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6330.6 | 6330.6 | 6.71 | 4
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3358.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3967.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4625.8 | 4625.8 | 6.73 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 5465.5 | 5465.5 | 6.83 | 4
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3764.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4470.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5184.9 | 5184.9 | 6.87 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6158.1 | 6158.1 | 6.73 | 4
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4690.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5570.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6461 | 6461 | 6.69 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 7672.5 | 7672.5 | 6.73 | 4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4645.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5075.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6398.3 | 6398.3 | 6.7 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6990.9 | 6990.9 | 6.81 | 4
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 7050.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 7390.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9711.2 | 9711.2 | 6.81 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10180.2 | 10180.2 | 6.77 | 4
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3656.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4207.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5036.6 | 5036.6 | 6.66 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 5795.4 | 5795.4 | 6.78 | 4
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5063.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5936.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6974.6 | 6974.6 | 6.81 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 8176.6 | 8176.6 | 6.83 | 4
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3865.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4687.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5324.3 | 5324.3 | 6.85 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6456.5 | 6456.5 | 6.69 | 4
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5313.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6347.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 7318.4 | 7318.4 | 6.77 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 8742.8 | 8742.8 | 6.77 | 4
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5001.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5689.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6889.7 | 6889.7 | 6.82 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 7836.8 | 7836.8 | 6.71 | 4
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 6692.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 7642.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9218.4 | 9218.4 | 6.73 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10527 | 10527 | 6.75 | 4
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3751 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4786.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5166.7 | 5166.7 | 6.87 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6593 | 6593 | 6.68 | 4
DX Heating Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 2401.6 | 2401.6 | 6.94 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 2400.4 | 2400.4 | 6.94 | 4
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4247.9 | 4247.9 | 6.8 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 4890.8 | 4890.8 | 6.69 | 4
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4468.5 | 4468.5 | 6.75 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 5164.1 | 5164.1 | 6.88 | 4
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5231.5 | 5231.5 | 6.86 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6330.6 | 6330.6 | 6.71 | 4
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4625.8 | 4625.8 | 6.73 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 5465.5 | 5465.5 | 6.83 | 4
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5184.9 | 5184.9 | 6.87 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6158.1 | 6158.1 | 6.73 | 4
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6461 | 6461 | 6.69 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 7672.5 | 7672.5 | 6.73 | 4
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6398.3 | 6398.3 | 6.7 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6990.9 | 6990.9 | 6.81 | 4
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9711.2 | 9711.2 | 6.81 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10180.2 | 10180.2 | 6.77 | 4
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5036.6 | 5036.6 | 6.66 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 5795.4 | 5795.4 | 6.78 | 4
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6974.6 | 6974.6 | 6.81 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 8176.6 | 8176.6 | 6.83 | 4
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5324.3 | 5324.3 | 6.85 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6456.5 | 6456.5 | 6.69 | 4
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 7318.4 | 7318.4 | 6.77 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 8742.8 | 8742.8 | 6.77 | 4
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 6889.7 | 6889.7 | 6.82 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 7836.8 | 7836.8 | 6.71 | 4
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9218.4 | 9218.4 | 6.73 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10527 | 10527 | 6.75 | 4
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 5166.7 | 5166.7 | 6.87 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 6593 | 6593 | 6.68 | 4
SWHC049-03 SEER Rated AC HP_SFm_1985 | SFm&1&rDXGF&Ex&dxAC_equip | dxAC-Res-SEER-13.0
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXGF EL7 | Heating | Sensible | 3139.45 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ01 | 3 | DXGF EL8 | Cooling | Sensible | 245.72 | 0.0189 | 0.0189 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL8 | Heating | Sensible | 3137.92 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ02 | 1 | DXGF EL7 | Cooling | Sensible | 2298.09 | 0.12931 | 0.12931 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL7 | Heating | Sensible | 2919.78 | 0.0755 | 0.0755 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 45313
CZ02 | 3 | DXGF EL8 | Cooling | Sensible | 2645.89 | 0.14887 | 0.14887 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL8 | Heating | Sensible | 2915.19 | 0.0754 | 0.0754 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 45313
CZ03 | 1 | DXGF EL7 | Cooling | Sensible | 1951.09 | 0.13602 | 0.13602 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL7 | Heating | Sensible | 3794.26 | 0.0993 | 0.0993 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL8 | Cooling | Sensible | 2254.8 | 0.1572 | 0.1572 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL8 | Heating | Sensible | 3791.65 | 0.0992 | 0.0992 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL7 | Cooling | Sensible | 2795.59 | 0.15925 | 0.15925 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL7 | Heating | Sensible | 4065.06 | 0.10626 | 0.10626 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL8 | Cooling | Sensible | 3343.38 | 0.1927 | 0.1927 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL8 | Heating | Sensible | 4063.31 | 0.10621 | 0.10621 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL7 | Cooling | Sensible | 2008.9 | 0.14081 | 0.14081 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL7 | Heating | Sensible | 4371.25 | 0.11504 | 0.11504 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ05 | 3 | DXGF EL8 | Cooling | Sensible | 2373.55 | 0.16637 | 0.16637 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL8 | Heating | Sensible | 4368.22 | 0.11496 | 0.11496 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ06 | 1 | DXGF EL7 | Cooling | Sensible | 2348.21 | 0.15783 | 0.15783 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL7 | Heating | Sensible | 1784.48 | 0.0448 | 0.0448 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL8 | Cooling | Sensible | 2789 | 0.18745 | 0.18745 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL8 | Heating | Sensible | 1783.75 | 0.0447 | 0.0447 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL7 | Cooling | Sensible | 2967.58 | 0.19667 | 0.19667 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL7 | Heating | Sensible | 1214.97 | 0.0292 | 0.0292 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ07 | 3 | DXGF EL8 | Cooling | Sensible | 3557.32 | 0.23355 | 0.23355 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL8 | Heating | Sensible | 1213.67 | 0.0291 | 0.0291 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ08 | 1 | DXGF EL7 | Cooling | Sensible | 3069.23 | 0.19476 | 0.19476 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL7 | Heating | Sensible | 1660.53 | 0.0399 | 0.0399 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ08 | 3 | DXGF EL8 | Cooling | Sensible | 3490.4 | 0.2128 | 0.2128 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL8 | Heating | Sensible | 1659.73 | 0.0399 | 0.0399 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:10
CZ09 | 1 | DXGF EL7 | Cooling | Sensible | 4438.4 | 0.29561 | 0.29561 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL7 | Heating | Sensible | 4846.73 | 0.13379 | 0.13379 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL8 | Cooling | Sensible | 4823 | 0.30988 | 0.30988 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL8 | Heating | Sensible | 4846.64 | 0.13379 | 0.13379 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL7 | Cooling | Sensible | 2750.25 | 0.15331 | 0.15331 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL7 | Heating | Sensible | 3308.71 | 0.0939 | 0.0939 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL8 | Cooling | Sensible | 3158.56 | 0.17641 | 0.17641 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL8 | Heating | Sensible | 3307.65 | 0.0938 | 0.0938 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL7 | Cooling | Sensible | 3623.66 | 0.21231 | 0.21231 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL7 | Heating | Sensible | 4997.83 | 0.13879 | 0.13879 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL8 | Cooling | Sensible | 4239.99 | 0.2489 | 0.2489 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL8 | Heating | Sensible | 4996.37 | 0.13875 | 0.13875 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL7 | Cooling | Sensible | 2808.12 | 0.16207 | 0.16207 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL7 | Heating | Sensible | 4574.79 | 0.12612 | 0.12612 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL8 | Cooling | Sensible | 3399.36 | 0.19654 | 0.19654 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL8 | Heating | Sensible | 4568.38 | 0.12594 | 0.12594 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL7 | Cooling | Sensible | 3872.04 | 0.22277 | 0.22277 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL7 | Heating | Sensible | 4369.72 | 0.12177 | 0.12177 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL8 | Cooling | Sensible | 4555.7 | 0.26613 | 0.26613 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL8 | Heating | Sensible | 4368.47 | 0.12174 | 0.12174 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL7 | Cooling | Sensible | 3733.5 | 0.20972 | 0.20972 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL7 | Heating | Sensible | 2487.89 | 0.0802 | 0.0802 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL8 | Cooling | Sensible | 4246.74 | 0.23855 | 0.23855 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL8 | Heating | Sensible | 2486.17 | 0.0801 | 0.0801 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL7 | Cooling | Sensible | 4943.05 | 0.28061 | 0.28061 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL7 | Heating | Sensible | 3487.47 | 0.0995 | 0.0995 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL8 | Cooling | Sensible | 5582.92 | 0.32044 | 0.32044 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL8 | Heating | Sensible | 3483.87 | 0.0994 | 0.0994 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL7 | Cooling | Sensible | 2325.75 | 0.15727 | 0.15727 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL7 | Heating | Sensible | 4159.68 | 0.11252 | 0.11252 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXGF EL8 | Cooling | Sensible | 2983.35 | 0.20069 | 0.20069 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL8 | Heating | Sensible | 4160.68 | 0.11255 | 0.11255 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 1143.4 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 1142.9 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2371.9 | 2.71 | 9.26 | 10.49 | 9.92 | 10.3
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 2731.4 | 2.71 | 9.26 | 10.49 | 9.92 | 10.3
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2136.1 | 2.65 | 9.04 | 10.21 | 9.66 | 9.88
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 2458.7 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2897.9 | 2.71 | 9.25 | 10.47 | 9.91 | 10.27
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3462.1 | 2.71 | 9.23 | 10.45 | 9.89 | 10.24
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2202.4 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 2602.2 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2468.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 2932 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3235.9 | 2.67 | 9.11 | 10.29 | 9.74 | 10.01
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3832.3 | 2.67 | 9.1 | 10.29 | 9.73 | 10
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3290.6 | 2.68 | 9.15 | 10.34 | 9.78 | 10.08
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3708.3 | 2.69 | 9.19 | 10.4 | 9.84 | 10.16
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4639.7 | 2.65 | 9.03 | 10.21 | 9.66 | 9.88
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5028.7 | 2.66 | 9.09 | 10.27 | 9.71 | 9.97
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3148.1 | 2.76 | 9.41 | 10.67 | 10.1 | 10.58
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3569.9 | 2.75 | 9.4 | 10.65 | 10.07 | 10.54
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3995.7 | 2.73 | 9.3 | 10.53 | 9.96 | 10.36
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4672.6 | 2.72 | 9.3 | 10.53 | 9.96 | 10.35
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3158 | 2.74 | 9.35 | 10.59 | 10.02 | 10.45
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3796.8 | 2.74 | 9.33 | 10.57 | 10 | 10.43
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4422.8 | 2.75 | 9.37 | 10.62 | 10.05 | 10.5
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5166.9 | 2.74 | 9.34 | 10.58 | 10.01 | 10.44
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4266.6 | 2.76 | 9.4 | 10.66 | 10.08 | 10.56
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4809 | 2.75 | 9.39 | 10.64 | 10.07 | 10.53
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5687.4 | 2.75 | 9.4 | 10.65 | 10.08 | 10.55
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6409.6 | 2.75 | 9.38 | 10.63 | 10.06 | 10.51
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2552.3 | 2.66 | 9.09 | 10.27 | 9.71 | 9.97
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3280.7 | 2.67 | 9.1 | 10.28 | 9.73 | 9.99
SWHC049-03 SEER Rated AC HP_MFm_Ex | MFm&0&rDXHP&Ex&dxHP_equip | HSPF_7p0_SEER_13_Pre
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1099.1 | 0.0264 | 0.0264 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 1473.72 | 0.0959 | 0.0959 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3041.93 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 135.57 | 0.00326 | 0.00326 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 1376.08 | 0.0896 | 0.0896 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2172.84 | 0.0522 | 0.0522 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 902.87 | 0.0217 | 0.0217 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 1095.24 | 0.0713 | 0.0713 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3112.59 | 0.0748 | 0.0748 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1109.59 | 0.0267 | 0.0267 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 4318.65 | 0.28116 | 0.28116 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3050.38 | 0.0733 | 0.0733 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 141.24 | 0.0034 | 0.0034 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 4303.58 | 0.28018 | 0.28018 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2181.46 | 0.0524 | 0.0524 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 908.23 | 0.0218 | 0.0218 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 4309.5 | 0.28056 | 0.28056 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3118.64 | 0.075 | 0.075 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1107.96 | 0.0266 | 0.0266 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 4148.96 | 0.27011 | 0.27011 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3048.89 | 0.0733 | 0.0733 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 135.58 | 0.00326 | 0.00326 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 398.22 | 0.0259 | 0.0259 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2172.82 | 0.0522 | 0.0522 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 893.4 | 0.0215 | 0.0215 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 2275.33 | 0.14813 | 0.14813 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3102.56 | 0.0746 | 0.0746 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 898.79 | 0.0216 | 0.0216 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 2301.52 | 0.14984 | 0.14984 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3112.96 | 0.0748 | 0.0748 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 141.25 | 0.0034 | 0.0034 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 384.73 | 0.025 | 0.025 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2181.54 | 0.0525 | 0.0525 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1118.45 | 0.0269 | 0.0269 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 4145.71 | 0.2699 | 0.2699 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3057.34 | 0.0735 | 0.0735 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ02 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1086.35 | 0.0623 | 0.0623 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 236.6 | 0.00653 | 0.00653 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4354.14 | 0.25238 | 0.25238 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4674 | 0.12877 | 0.12877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 879.28 | 0.0515 | 0.0515 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3725.8 | 0.21815 | 0.21815 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3443.86 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1131.11 | 0.0652 | 0.0652 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 609.11 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4403.69 | 0.25399 | 0.25399 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4642.6 | 0.12774 | 0.12774 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1071.46 | 0.0615 | 0.0615 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 236.6 | 0.00653 | 0.00653 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7110.44 | 0.41722 | 0.41722 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4673.99 | 0.12877 | 0.12877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 862.9 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6631.78 | 0.38914 | 0.38914 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3443.77 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1115.98 | 0.0643 | 0.0643 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 609.1 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7117.92 | 0.41766 | 0.41766 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4639.92 | 0.12767 | 0.12767 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1070.32 | 0.0614 | 0.0614 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 231.05 | 0.00638 | 0.00638 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7110.83 | 0.41706 | 0.41706 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4676.62 | 0.12884 | 0.12884 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 861.8 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3528.63 | 0.2066 | 0.2066 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3459.76 | 0.0953 | 0.0953 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1123.95 | 0.0647 | 0.0647 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 615.44 | 0.017 | 0.017 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4331.08 | 0.24973 | 0.24973 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4655.41 | 0.12809 | 0.12809 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1125.09 | 0.0648 | 0.0648 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 609.14 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4340.86 | 0.25029 | 0.25029 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4642.59 | 0.12774 | 0.12774 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 862.86 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3534.62 | 0.20695 | 0.20695 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3443.95 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1071.04 | 0.0614 | 0.0614 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 213.61 | 0.0059 | 0.0059 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7128.45 | 0.41809 | 0.41809 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4661.27 | 0.12842 | 0.12842 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ03 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 989.76 | 0.069 | 0.069 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2087.07 | 0.057 | 0.057 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3953.05 | 0.27559 | 0.27559 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3812.15 | 0.10449 | 0.10449 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 689.11 | 0.048 | 0.048 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1316.48 | 0.036 | 0.036 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3390.81 | 0.23639 | 0.23639 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2814.11 | 0.0772 | 0.0772 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1008.25 | 0.0703 | 0.0703 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2208.84 | 0.0607 | 0.0607 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3650.84 | 0.25452 | 0.25452 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3925.96 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 978.03 | 0.0682 | 0.0682 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2094.25 | 0.0572 | 0.0572 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 6721.41 | 0.46858 | 0.46858 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3814.53 | 0.10456 | 0.10456 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 678.26 | 0.0473 | 0.0473 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1323.29 | 0.0362 | 0.0362 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6321.6 | 0.4407 | 0.4407 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2816.45 | 0.0773 | 0.0773 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 996.71 | 0.0695 | 0.0695 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2215.8 | 0.0608 | 0.0608 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 6724.7 | 0.46881 | 0.46881 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3926.08 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 978.43 | 0.0682 | 0.0682 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2094.25 | 0.0572 | 0.0572 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6588.19 | 0.45929 | 0.45929 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3814.48 | 0.10456 | 0.10456 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 681.81 | 0.0475 | 0.0475 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1323.29 | 0.0362 | 0.0362 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2694.1 | 0.18782 | 0.18782 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2816.49 | 0.0773 | 0.0773 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1010.39 | 0.0704 | 0.0704 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2215.8 | 0.0608 | 0.0608 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4808.75 | 0.33525 | 0.33525 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3926.26 | 0.10795 | 0.10795 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1006.08 | 0.0701 | 0.0701 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2208.84 | 0.0607 | 0.0607 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4804.58 | 0.33495 | 0.33495 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3925.78 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 677.96 | 0.0473 | 0.0473 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1316.48 | 0.036 | 0.036 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2686.44 | 0.18728 | 0.18728 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2814.11 | 0.0772 | 0.0772 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 974.3 | 0.0679 | 0.0679 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2087.07 | 0.057 | 0.057 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6595.78 | 0.45982 | 0.45982 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3812.2 | 0.1045 | 0.1045 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ04 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1208.79 | 0.0693 | 0.0693 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 235.9 | 0.00676 | 0.00676 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4531.08 | 0.25999 | 0.25999 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3684.55 | 0.10557 | 0.10557 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 975.81 | 0.0571 | 0.0571 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3864.33 | 0.2262 | 0.2262 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2617.1 | 0.075 | 0.075 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1251.14 | 0.0721 | 0.0721 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 472.56 | 0.0135 | 0.0135 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4572.1 | 0.26364 | 0.26364 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3676.69 | 0.10535 | 0.10535 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1197.67 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 251.75 | 0.00722 | 0.00722 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7270.74 | 0.42653 | 0.42653 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3698.42 | 0.10597 | 0.10597 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 964.41 | 0.0565 | 0.0565 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6755.96 | 0.39633 | 0.39633 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2630.99 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1240.69 | 0.0714 | 0.0714 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 479.07 | 0.0137 | 0.0137 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7268.42 | 0.42639 | 0.42639 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3687.9 | 0.10567 | 0.10567 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1197.43 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 258.07 | 0.0074 | 0.0074 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7278.03 | 0.42676 | 0.42676 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3696.66 | 0.10592 | 0.10592 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 963.89 | 0.0564 | 0.0564 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3728.62 | 0.21826 | 0.21826 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2617.12 | 0.075 | 0.075 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1246.77 | 0.0718 | 0.0718 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 461.89 | 0.0132 | 0.0132 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4535.27 | 0.26145 | 0.26145 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3663.54 | 0.10497 | 0.10497 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1246.85 | 0.0718 | 0.0718 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 468.42 | 0.0134 | 0.0134 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4536.45 | 0.26151 | 0.26151 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3679.22 | 0.10542 | 0.10542 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 963.68 | 0.0564 | 0.0564 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3728.96 | 0.21828 | 0.21828 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2631.13 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1196.9 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 274.09 | 0.00785 | 0.00785 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7292.01 | 0.42758 | 0.42758 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3710.51 | 0.10631 | 0.10631 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ05 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 707.96 | 0.0474 | 0.0474 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2575.92 | 0.0716 | 0.0716 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3801.71 | 0.25469 | 0.25469 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4738.24 | 0.13162 | 0.13162 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 523.38 | 0.0351 | 0.0351 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1608.95 | 0.0447 | 0.0447 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3106.07 | 0.20809 | 0.20809 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3525.27 | 0.0979 | 0.0979 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 751.71 | 0.0504 | 0.0504 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2663.48 | 0.074 | 0.074 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3779.26 | 0.25319 | 0.25319 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4810.85 | 0.13364 | 0.13364 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 690.9 | 0.0463 | 0.0463 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2589.25 | 0.0719 | 0.0719 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7141.09 | 0.47842 | 0.47842 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4748.88 | 0.13192 | 0.13192 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 507.86 | 0.034 | 0.034 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1621.84 | 0.0451 | 0.0451 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6786.57 | 0.45467 | 0.45467 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3536.34 | 0.0982 | 0.0982 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 734.74 | 0.0492 | 0.0492 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2676.6 | 0.0744 | 0.0744 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7130 | 0.47768 | 0.47768 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4819.24 | 0.13388 | 0.13388 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 690.09 | 0.0462 | 0.0462 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2587.6 | 0.0719 | 0.0719 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6949.77 | 0.4656 | 0.4656 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4746.61 | 0.13185 | 0.13185 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 507.96 | 0.034 | 0.034 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1608.96 | 0.0447 | 0.0447 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2819.86 | 0.18892 | 0.18892 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3525.24 | 0.0979 | 0.0979 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 750.03 | 0.0502 | 0.0502 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2651.08 | 0.0736 | 0.0736 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4435.71 | 0.29716 | 0.29716 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4798.91 | 0.13331 | 0.13331 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 748.27 | 0.0501 | 0.0501 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2664.22 | 0.074 | 0.074 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4456.27 | 0.29854 | 0.29854 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4811.81 | 0.13367 | 0.13367 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 506.45 | 0.0339 | 0.0339 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1621.84 | 0.0451 | 0.0451 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2815.55 | 0.18863 | 0.18863 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3536.43 | 0.0982 | 0.0982 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 688.32 | 0.0461 | 0.0461 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2600.93 | 0.0723 | 0.0723 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6971.6 | 0.46706 | 0.46706 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4756.8 | 0.13214 | 0.13214 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ06 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1140.07 | 0.0733 | 0.0733 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1579.43 | 0.044 | 0.044 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4190.29 | 0.2695 | 0.2695 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3104.84 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 789.8 | 0.0508 | 0.0508 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1005.46 | 0.028 | 0.028 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3637.27 | 0.23393 | 0.23393 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2324.94 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1166.78 | 0.075 | 0.075 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1596.84 | 0.0445 | 0.0445 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3915.88 | 0.25185 | 0.25185 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3100.71 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1131.13 | 0.0727 | 0.0727 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1584.05 | 0.0441 | 0.0441 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 6880.25 | 0.44251 | 0.44251 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3105.58 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 781.41 | 0.0503 | 0.0503 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1010.14 | 0.0282 | 0.0282 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6454.17 | 0.41511 | 0.41511 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2325.61 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1157.86 | 0.0745 | 0.0745 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1601.53 | 0.0446 | 0.0446 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 6892.49 | 0.4433 | 0.4433 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3099.32 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1130.97 | 0.0727 | 0.0727 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1584.05 | 0.0441 | 0.0441 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6745.51 | 0.43384 | 0.43384 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3105.52 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 781.08 | 0.0502 | 0.0502 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1010.14 | 0.0282 | 0.0282 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2899.41 | 0.18648 | 0.18648 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2325.64 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1162.77 | 0.0748 | 0.0748 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1601.53 | 0.0446 | 0.0446 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5048.39 | 0.32469 | 0.32469 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3099.49 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1166.08 | 0.075 | 0.075 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1596.84 | 0.0445 | 0.0445 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5082.25 | 0.32687 | 0.32687 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3100.55 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 784.14 | 0.0504 | 0.0504 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1005.46 | 0.028 | 0.028 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2909.63 | 0.18714 | 0.18714 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2324.94 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1134.25 | 0.073 | 0.073 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1579.42 | 0.044 | 0.044 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6771.29 | 0.4355 | 0.4355 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3104.9 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 854.64 | 0.0521 | 0.0521 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1838.53 | 0.0517 | 0.0517 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3928.28 | 0.23023 | 0.23023 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3584.36 | 0.1007 | 0.1007 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 793.25 | 0.0484 | 0.0484 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1256.85 | 0.0353 | 0.0353 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3503.71 | 0.21311 | 0.21311 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2811.52 | 0.079 | 0.079 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 919.84 | 0.0533 | 0.0533 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1858.87 | 0.0522 | 0.0522 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3868.28 | 0.22527 | 0.22527 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3577.52 | 0.10051 | 0.10051 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 849.68 | 0.0518 | 0.0518 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1828.63 | 0.0514 | 0.0514 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7274.8 | 0.43506 | 0.43506 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3575.13 | 0.10044 | 0.10044 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 787.03 | 0.048 | 0.048 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1246.84 | 0.035 | 0.035 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6918.14 | 0.4147 | 0.4147 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2801.94 | 0.0787 | 0.0787 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 910.01 | 0.0528 | 0.0528 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1848.4 | 0.0519 | 0.0519 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7281.97 | 0.4357 | 0.4357 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3565.72 | 0.10017 | 0.10017 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 849.24 | 0.0518 | 0.0518 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1829.7 | 0.0514 | 0.0514 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7073.66 | 0.42435 | 0.42435 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3576.27 | 0.10047 | 0.10047 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 786.32 | 0.0479 | 0.0479 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1256.84 | 0.0353 | 0.0353 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3283.54 | 0.19721 | 0.19721 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2811.48 | 0.079 | 0.079 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 921.44 | 0.0534 | 0.0534 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1869.33 | 0.0525 | 0.0525 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4920.36 | 0.29956 | 0.29956 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3583.3 | 0.10067 | 0.10067 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 918.97 | 0.0532 | 0.0532 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1858.88 | 0.0522 | 0.0522 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4982.93 | 0.30388 | 0.30388 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3575.99 | 0.10046 | 0.10046 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 785.21 | 0.0479 | 0.0479 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1246.84 | 0.035 | 0.035 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3294.38 | 0.19787 | 0.19787 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2802.02 | 0.0787 | 0.0787 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 848.17 | 0.0517 | 0.0517 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1819.8 | 0.0511 | 0.0511 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7106.84 | 0.42739 | 0.42739 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3567.04 | 0.10021 | 0.10021 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1361.99 | 0.0768 | 0.0768 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1658.92 | 0.0458 | 0.0458 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4861.67 | 0.27861 | 0.27861 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3325.81 | 0.0917 | 0.0917 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1091.07 | 0.0664 | 0.0664 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 960.95 | 0.0265 | 0.0265 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4101.98 | 0.24115 | 0.24115 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2444.9 | 0.0674 | 0.0674 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1462.88 | 0.0841 | 0.0841 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1679.26 | 0.0463 | 0.0463 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4926.55 | 0.28198 | 0.28198 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3310.11 | 0.0913 | 0.0913 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1354.51 | 0.0766 | 0.0766 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1647.36 | 0.0454 | 0.0454 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 8649.25 | 0.51748 | 0.51748 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3314.64 | 0.0914 | 0.0914 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1085.98 | 0.0662 | 0.0662 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 949.47 | 0.0262 | 0.0262 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8069.44 | 0.48503 | 0.48503 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2433.32 | 0.0671 | 0.0671 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1456.28 | 0.0837 | 0.0837 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1667.64 | 0.046 | 0.046 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 8659.78 | 0.52043 | 0.52043 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3296.29 | 0.0909 | 0.0909 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1353.19 | 0.0764 | 0.0764 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1648.46 | 0.0455 | 0.0455 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 8444.71 | 0.5044 | 0.5044 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3315.95 | 0.0915 | 0.0915 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1084.41 | 0.0661 | 0.0661 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 960.95 | 0.0265 | 0.0265 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4017.14 | 0.23616 | 0.23616 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2444.85 | 0.0674 | 0.0674 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1462.46 | 0.0841 | 0.0841 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1689.94 | 0.0466 | 0.0466 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5561.88 | 0.33402 | 0.33402 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3317.58 | 0.0915 | 0.0915 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1461.91 | 0.084 | 0.084 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1678.36 | 0.0463 | 0.0463 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5615.93 | 0.33733 | 0.33733 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3308.35 | 0.0913 | 0.0913 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1084.3 | 0.0661 | 0.0661 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 949.47 | 0.0262 | 0.0262 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4018.65 | 0.24142 | 0.24142 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2433.4 | 0.0671 | 0.0671 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1352.18 | 0.0764 | 0.0764 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1636.91 | 0.0452 | 0.0452 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 8467.53 | 0.50947 | 0.50947 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3304.77 | 0.0912 | 0.0912 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1501.7 | 0.0844 | 0.0844 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1794.2 | 0.0527 | 0.0527 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5608.08 | 0.32143 | 0.32143 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3442.09 | 0.10107 | 0.10107 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1144.97 | 0.0674 | 0.0674 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1064.86 | 0.0313 | 0.0313 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4749.6 | 0.27826 | 0.27826 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2551.98 | 0.0749 | 0.0749 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1574.08 | 0.0892 | 0.0892 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1829.27 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5659.97 | 0.32445 | 0.32445 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3436.6 | 0.1009 | 0.1009 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1497.33 | 0.0842 | 0.0842 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9578.91 | 0.56467 | 0.56467 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3436.88 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1139.28 | 0.0671 | 0.0671 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8930.06 | 0.52642 | 0.52642 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2546.55 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1569.16 | 0.0889 | 0.0889 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1825.32 | 0.0536 | 0.0536 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9582.38 | 0.56488 | 0.56488 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3428.53 | 0.10067 | 0.10067 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1495.44 | 0.084 | 0.084 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9460.95 | 0.55755 | 0.55755 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3436.8 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1138.34 | 0.067 | 0.067 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4668.74 | 0.27439 | 0.27439 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2546.56 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1572.58 | 0.0891 | 0.0891 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1829 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6606.44 | 0.38921 | 0.38921 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3433.16 | 0.1008 | 0.1008 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1572.73 | 0.0891 | 0.0891 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1829.02 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6671.38 | 0.39304 | 0.39304 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3435.54 | 0.10087 | 0.10087 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1138.47 | 0.0671 | 0.0671 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4670.2 | 0.27448 | 0.27448 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2546.61 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1495.49 | 0.0841 | 0.0841 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9481.42 | 0.55876 | 0.55876 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3436.83 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ10 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1935.26 | 0.10801 | 0.10801 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1835.28 | 0.0521 | 0.0521 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5422.33 | 0.3026 | 0.3026 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3791.73 | 0.10757 | 0.10757 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1342.55 | 0.0749 | 0.0749 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1007.79 | 0.0286 | 0.0286 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4220.51 | 0.23554 | 0.23554 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2773.66 | 0.0787 | 0.0787 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1970.15 | 0.10997 | 0.10997 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1879.67 | 0.0533 | 0.0533 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5431.58 | 0.30312 | 0.30312 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3796.69 | 0.10771 | 0.10771 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1926.57 | 0.10753 | 0.10753 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1848.49 | 0.0524 | 0.0524 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 8681.24 | 0.49635 | 0.49635 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3805.04 | 0.10795 | 0.10795 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1333.47 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1020.89 | 0.029 | 0.029 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 7940.66 | 0.45502 | 0.45502 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2787.13 | 0.0791 | 0.0791 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1961.52 | 0.10949 | 0.10949 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1892.89 | 0.0537 | 0.0537 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 8707.38 | 0.49805 | 0.49805 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3807.57 | 0.10802 | 0.10802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1924.92 | 0.10743 | 0.10743 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1847.15 | 0.0524 | 0.0524 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 8512.05 | 0.48375 | 0.48375 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3803.3 | 0.1079 | 0.1079 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1331.99 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1007.79 | 0.0286 | 0.0286 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4013.15 | 0.22397 | 0.22397 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2773.64 | 0.0787 | 0.0787 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1965.5 | 0.10971 | 0.10971 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1867.52 | 0.053 | 0.053 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5368.62 | 0.2996 | 0.2996 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3782.98 | 0.10732 | 0.10732 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1965.72 | 0.10972 | 0.10972 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1880.76 | 0.0534 | 0.0534 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5374.67 | 0.29994 | 0.29994 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3798.48 | 0.10776 | 0.10776 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1332.25 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1020.9 | 0.029 | 0.029 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4026.23 | 0.22978 | 0.22978 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2787.22 | 0.0791 | 0.0791 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1925.11 | 0.10744 | 0.10744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1860.37 | 0.0528 | 0.0528 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 8542.23 | 0.48547 | 0.48547 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3816.61 | 0.10828 | 0.10828 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 2324.58 | 0.13338 | 0.13338 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 774.34 | 0.0212 | 0.0212 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 6458.99 | 0.37501 | 0.37501 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4534.77 | 0.12394 | 0.12394 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1692.96 | 0.1013 | 0.1013 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 5284.41 | 0.31923 | 0.31923 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3310.7 | 0.0904 | 0.0904 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 2389.62 | 0.14133 | 0.14133 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 996.68 | 0.0273 | 0.0273 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 6533.13 | 0.38589 | 0.38589 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4538.03 | 0.12401 | 0.12401 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 2315.78 | 0.13287 | 0.13287 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 771.13 | 0.0211 | 0.0211 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9763.15 | 0.60132 | 0.60132 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4536.25 | 0.12398 | 0.12398 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1684.18 | 0.10222 | 0.10222 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8754.4 | 0.5392 | 0.5392 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3311.97 | 0.0905 | 0.0905 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 2382.24 | 0.14089 | 0.14089 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 994.16 | 0.0272 | 0.0272 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9779.78 | 0.60234 | 0.60234 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4537.35 | 0.12399 | 0.12399 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 2317.85 | 0.13299 | 0.13299 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 770.22 | 0.0211 | 0.0211 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9534.99 | 0.58616 | 0.58616 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4536.2 | 0.12398 | 0.12398 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1686.53 | 0.10092 | 0.10092 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 5218.75 | 0.31756 | 0.31756 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3310.67 | 0.0904 | 0.0904 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 2388.15 | 0.14123 | 0.14123 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1000.82 | 0.0274 | 0.0274 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6528.1 | 0.40101 | 0.40101 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4534.58 | 0.12391 | 0.12391 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 2385.93 | 0.1411 | 0.1411 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 998.31 | 0.0273 | 0.0273 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6708.14 | 0.41212 | 0.41212 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4537.89 | 0.124 | 0.124 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1684.36 | 0.10079 | 0.10079 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 5217.1 | 0.31746 | 0.31746 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3312.04 | 0.0905 | 0.0905 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 2315.74 | 0.13287 | 0.13287 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 767.01 | 0.021 | 0.021 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9571.33 | 0.58785 | 0.58785 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4537.69 | 0.12402 | 0.12402 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1217.43 | 0.0638 | 0.0638 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2133.43 | 0.0566 | 0.0566 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4738.9 | 0.2484 | 0.2484 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4380.11 | 0.11835 | 0.11835 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 919.45 | 0.0482 | 0.0482 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1155.63 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3694.95 | 0.19368 | 0.19368 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3442.08 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1273.03 | 0.0667 | 0.0667 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2238.21 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4770.61 | 0.25006 | 0.25006 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4618.07 | 0.12484 | 0.12484 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1203.14 | 0.0631 | 0.0631 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2147.85 | 0.057 | 0.057 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7633.78 | 0.40013 | 0.40013 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4391.06 | 0.11865 | 0.11865 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 905.96 | 0.0475 | 0.0475 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1167.49 | 0.0315 | 0.0315 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 7029.78 | 0.36847 | 0.36847 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3453.68 | 0.0933 | 0.0933 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1258.87 | 0.066 | 0.066 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2251.31 | 0.0604 | 0.0604 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7704.02 | 0.40382 | 0.40382 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4628.59 | 0.12512 | 0.12512 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1201.58 | 0.063 | 0.063 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2145.41 | 0.0569 | 0.0569 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7456.78 | 0.39086 | 0.39086 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4388.86 | 0.11859 | 0.11859 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 902.55 | 0.0473 | 0.0473 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1155.6 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3523.12 | 0.18467 | 0.18467 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3441.96 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1266.43 | 0.0664 | 0.0664 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2238.14 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4720.68 | 0.24744 | 0.24744 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4615.52 | 0.12477 | 0.12477 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1268.87 | 0.0665 | 0.0665 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2238.16 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4736.3 | 0.24826 | 0.24826 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4617.78 | 0.12483 | 0.12483 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 905.3 | 0.0475 | 0.0475 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1155.6 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3538.11 | 0.18546 | 0.18546 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3442 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1204.21 | 0.0631 | 0.0631 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2145.4 | 0.0569 | 0.0569 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7573.43 | 0.39697 | 0.39697 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4388.81 | 0.11859 | 0.11859 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ13 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 3160 | 0.1946 | 0.1946 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2821.51 | 0.0786 | 0.0786 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 7493.53 | 0.46111 | 0.46111 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5210.03 | 0.14519 | 0.14519 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 2414.86 | 0.1488 | 0.1488 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1827.55 | 0.0509 | 0.0509 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 6178.75 | 0.38021 | 0.38021 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3913.36 | 0.10906 | 0.10906 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 3187.49 | 0.1963 | 0.1963 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2858.02 | 0.0796 | 0.0796 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 7505.47 | 0.46184 | 0.46184 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5159.42 | 0.14378 | 0.14378 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 3157.76 | 0.19446 | 0.19446 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2838.07 | 0.0791 | 0.0791 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 10452.21 | 0.64375 | 0.64375 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5226.79 | 0.14566 | 0.14566 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 2411.49 | 0.14859 | 0.14859 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1843.99 | 0.0514 | 0.0514 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 9327.16 | 0.5753 | 0.5753 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3930.64 | 0.10954 | 0.10954 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 3186.43 | 0.19623 | 0.19623 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2874.7 | 0.0801 | 0.0801 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 10439.15 | 0.64389 | 0.64389 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5173.82 | 0.14418 | 0.14418 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 3157.16 | 0.19443 | 0.19443 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2838.08 | 0.0791 | 0.0791 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 10594.47 | 0.6531 | 0.6531 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5226.72 | 0.14565 | 0.14565 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 2407.3 | 0.14833 | 0.14833 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1843.99 | 0.0514 | 0.0514 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 6099.82 | 0.37536 | 0.37536 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3930.68 | 0.10954 | 0.10954 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 3181.79 | 0.19595 | 0.19595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2874.7 | 0.0801 | 0.0801 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 7474.48 | 0.45993 | 0.45993 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5174.03 | 0.14419 | 0.14419 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 3186.62 | 0.19624 | 0.19624 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2858.02 | 0.0796 | 0.0796 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 7486.93 | 0.4607 | 0.4607 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5159.23 | 0.14377 | 0.14377 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 2411.21 | 0.14857 | 0.14857 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1827.55 | 0.0509 | 0.0509 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 6108.87 | 0.37591 | 0.37591 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3913.37 | 0.10906 | 0.10906 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 3160.93 | 0.19466 | 0.19466 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2821.51 | 0.0786 | 0.0786 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 10691.91 | 0.65911 | 0.65911 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5210.08 | 0.14519 | 0.14519 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ14 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 2550.11 | 0.13839 | 0.13839 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1255.15 | 0.0371 | 0.0371 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 6043.55 | 0.32798 | 0.32798 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4640.41 | 0.1371 | 0.1371 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1660.91 | 0.0901 | 0.0901 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4531.32 | 0.24592 | 0.24592 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3248.15 | 0.096 | 0.096 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 2597.63 | 0.14097 | 0.14097 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1230.55 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 6074.5 | 0.32966 | 0.32966 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4621.83 | 0.13655 | 0.13655 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 2549.93 | 0.13838 | 0.13838 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1252.94 | 0.037 | 0.037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9161.94 | 0.49722 | 0.49722 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4646.24 | 0.13727 | 0.13727 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1661.63 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8143.58 | 0.44195 | 0.44195 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3253.72 | 0.0961 | 0.0961 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 2597.98 | 0.14099 | 0.14099 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1228.86 | 0.0363 | 0.0363 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9256.32 | 0.50234 | 0.50234 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4625.37 | 0.13666 | 0.13666 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 2549.11 | 0.13834 | 0.13834 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1252.33 | 0.037 | 0.037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9098.54 | 0.49378 | 0.49378 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4645.81 | 0.13726 | 0.13726 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1655.22 | 0.0898 | 0.0898 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4459.04 | 0.24199 | 0.24199 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3248.13 | 0.096 | 0.096 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 2591.4 | 0.14064 | 0.14064 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1233.36 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6255.41 | 0.33948 | 0.33948 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4614.54 | 0.13634 | 0.13634 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 2597.15 | 0.14095 | 0.14095 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1231.68 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6394.27 | 0.34702 | 0.34702 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4621.95 | 0.13655 | 0.13655 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1661.22 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4472.48 | 0.24272 | 0.24272 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3253.79 | 0.0961 | 0.0961 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 2554.89 | 0.13865 | 0.13865 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1250.13 | 0.0369 | 0.0369 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9225.36 | 0.50066 | 0.50066 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4651.63 | 0.13743 | 0.13743 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ15 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 3231.07 | 0.18011 | 0.18011 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2112.65 | 0.0592 | 0.0592 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 7725.48 | 0.43652 | 0.43652 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3985.59 | 0.11169 | 0.11169 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 2294.73 | 0.13738 | 0.13738 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1249.24 | 0.035 | 0.035 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 6237.95 | 0.36318 | 0.36318 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2899.51 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 3315.63 | 0.18912 | 0.18912 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2155.46 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 7793.71 | 0.44419 | 0.44419 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3970.98 | 0.11128 | 0.11128 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 3227.41 | 0.1799 | 0.1799 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2108.09 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 11297.85 | 0.6793 | 0.6793 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3987.23 | 0.11174 | 0.11174 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 2291.52 | 0.13719 | 0.13719 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 10045.94 | 0.60553 | 0.60553 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2901.01 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 3311.78 | 0.1889 | 0.1889 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2150.9 | 0.0603 | 0.0603 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 11412.33 | 0.69066 | 0.69066 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3970.47 | 0.11127 | 0.11127 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 3225.6 | 0.17981 | 0.17981 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2108.08 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 11086.8 | 0.66389 | 0.66389 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3987.19 | 0.11173 | 0.11173 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 2291.28 | 0.13717 | 0.13717 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 6190.58 | 0.36283 | 0.36283 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2901.05 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 3315.32 | 0.18909 | 0.18909 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2154.9 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 7936.76 | 0.47468 | 0.47468 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3969.12 | 0.11123 | 0.11123 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 3315.67 | 0.18911 | 0.18911 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2154.92 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 8121.34 | 0.49396 | 0.49396 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3970.87 | 0.11128 | 0.11128 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 2291.57 | 0.13719 | 0.13719 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 6243.57 | 0.37944 | 0.37944 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2901.08 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 3225.81 | 0.17982 | 0.17982 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2108.08 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 11245.78 | 0.68125 | 0.68125 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3987.24 | 0.11174 | 0.11174 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ16 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1814.63 | 0.11967 | 0.11967 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3072.15 | 0.0901 | 0.0901 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5812.15 | 0.38797 | 0.38797 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5533.51 | 0.16236 | 0.16236 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1290.73 | 0.0877 | 0.0877 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4750.24 | 0.32459 | 0.32459 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 4000.07 | 0.11737 | 0.11737 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1866.13 | 0.12362 | 0.12362 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3094.06 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5870.5 | 0.39393 | 0.39393 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5528.31 | 0.16221 | 0.16221 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1799.01 | 0.11864 | 0.11864 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3072.15 | 0.0901 | 0.0901 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9533.45 | 0.67542 | 0.67542 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5533.56 | 0.16236 | 0.16236 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1275.64 | 0.0869 | 0.0869 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8739.6 | 0.61918 | 0.61918 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 4000.01 | 0.11736 | 0.11736 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1851.97 | 0.12288 | 0.12288 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3094.05 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9619.84 | 0.68153 | 0.68153 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5526.26 | 0.16215 | 0.16215 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1797.79 | 0.11856 | 0.11856 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3072.96 | 0.0902 | 0.0902 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9295.91 | 0.65636 | 0.65636 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5533.15 | 0.16235 | 0.16235 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1274.25 | 0.0868 | 0.0868 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1691.34 | 0.0496 | 0.0496 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4589.08 | 0.31733 | 0.31733 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3995.49 | 0.11723 | 0.11723 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1862.69 | 0.12358 | 0.12358 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3099.4 | 0.0909 | 0.0909 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5810.41 | 0.39288 | 0.39288 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5521.88 | 0.16202 | 0.16202 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1861.04 | 0.12326 | 0.12326 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3094.07 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5822.54 | 0.39768 | 0.39768 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5528.14 | 0.1622 | 0.1622 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1272.88 | 0.0867 | 0.0867 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4608.96 | 0.32184 | 0.32184 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 4000.07 | 0.11737 | 0.11737 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1796.51 | 0.11847 | 0.11847 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3067.6 | 0.09 | 0.09 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9416.37 | 0.66711 | 0.66711 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5537.74 | 0.16248 | 0.16248 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 630.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 2305.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 77.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 2136.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 517.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 1863.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 636.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 6705.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 81 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6682.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 520.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 6691.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 635.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 6741.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 77.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 1246 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 512.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 3750.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 515.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 3803.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 81 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 1251 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 641.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 6747.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 868.1 | 868.1 | 7.07 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 3176.1 | 3176.1 | 6.7 | 4
CZ01 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 107.1 | 107.1 | 3.9 | 4
CZ01 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 2943.1 | 2943.1 | 6.76 | 4
CZ01 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 713.1 | 713.1 | 6.91 | 4
CZ01 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 2567.3 | 2567.3 | 6.88 | 4
CZ01 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 876.4 | 876.4 | 7.07 | 4
CZ01 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 9236.6 | 9236.6 | 6.73 | 4
CZ01 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 111.6 | 111.6 | 3.93 | 4
CZ01 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 9204.3 | 9204.3 | 6.73 | 4
CZ01 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 717.4 | 717.4 | 6.92 | 4
CZ01 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 9217 | 9217 | 6.73 | 4
CZ01 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 875.1 | 875.1 | 7.07 | 4
CZ01 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 9286.4 | 9286.4 | 6.72 | 4
CZ01 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 107.1 | 107.1 | 3.9 | 4
CZ01 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 1716.2 | 1716.2 | 6.65 | 4
CZ01 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 705.7 | 705.7 | 6.88 | 4
CZ01 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 5166.2 | 5166.2 | 6.87 | 4
CZ01 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 709.9 | 709.9 | 6.9 | 4
CZ01 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 5238.9 | 5238.9 | 6.86 | 4
CZ01 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 111.6 | 111.6 | 3.93 | 4
CZ01 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 1723.1 | 1723.1 | 6.65 | 4
CZ01 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 883.4 | 883.4 | 7.08 | 4
CZ01 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 9294.5 | 9294.5 | 6.72 | 4
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1486.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6019.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1228.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5202.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1554.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6057.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1466.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9950.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1205.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9281 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1533.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9961.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1464.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9946.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1203.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4927.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1544.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5956.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1545.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5969.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1205.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4935.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1465.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9971.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2047.5 | 2047.5 | 6.54 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8290.9 | 8290.9 | 6.82 | 4
CZ02 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1691.8 | 1691.8 | 6.66 | 4
CZ02 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7166.5 | 7166.5 | 6.79 | 4
CZ02 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2140.6 | 2140.6 | 6.51 | 4
CZ02 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8344.1 | 8344.1 | 6.81 | 4
CZ02 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2019.4 | 2019.4 | 6.54 | 4
CZ02 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 13706.5 | 13706.5 | 6.82 | 4
CZ02 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1660.3 | 1660.3 | 6.67 | 4
CZ02 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 12783.8 | 12783.8 | 6.7 | 4
CZ02 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2111.9 | 2111.9 | 6.52 | 4
CZ02 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 13720.9 | 13720.9 | 6.82 | 4
CZ02 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2017.2 | 2017.2 | 6.54 | 4
CZ02 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 13701 | 13701 | 6.82 | 4
CZ02 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1658.2 | 1658.2 | 6.67 | 4
CZ02 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6787.2 | 6787.2 | 6.83 | 4
CZ02 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2126.8 | 2126.8 | 6.51 | 4
CZ02 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 8204 | 8204 | 6.83 | 4
CZ02 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2129 | 2129 | 6.51 | 4
CZ02 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 8222.5 | 8222.5 | 6.82 | 4
CZ02 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1660.2 | 1660.2 | 6.67 | 4
CZ02 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6798.8 | 6798.8 | 6.83 | 4
CZ02 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2018.6 | 2018.6 | 6.54 | 4
CZ02 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 13735 | 13735 | 6.82 | 4
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1645.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6572.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1145.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5638 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1676.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6070.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1626.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 11175.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1127.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 10510.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1657.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 11181.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1626.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10954.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1133.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4479.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1680 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 7995.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1672.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 7988.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1127.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4466.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1620 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10966.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2266.8 | 2266.8 | 6.99 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 9053.5 | 9053.5 | 6.74 | 4
CZ03 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1578.2 | 1578.2 | 6.71 | 4
CZ03 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7765.8 | 7765.8 | 6.72 | 4
CZ03 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2309.1 | 2309.1 | 6.97 | 4
CZ03 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8361.3 | 8361.3 | 6.81 | 4
CZ03 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2239.9 | 2239.9 | 7 | 4
CZ03 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 15393.5 | 15393.5 | 6.73 | 4
CZ03 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1553.4 | 1553.4 | 6.72 | 4
CZ03 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14477.9 | 14477.9 | 6.78 | 4
CZ03 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2282.7 | 2282.7 | 6.98 | 4
CZ03 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 15401 | 15401 | 6.73 | 4
CZ03 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2240.8 | 2240.8 | 7 | 4
CZ03 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 15088.4 | 15088.4 | 6.74 | 4
CZ03 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1561.5 | 1561.5 | 6.72 | 4
CZ03 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6170.1 | 6170.1 | 6.73 | 4
CZ03 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2314 | 2314 | 6.97 | 4
CZ03 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 11013.3 | 11013.3 | 6.82 | 4
CZ03 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2304.2 | 2304.2 | 6.97 | 4
CZ03 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 11003.8 | 11003.8 | 6.82 | 4
CZ03 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1552.7 | 1552.7 | 6.72 | 4
CZ03 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6152.6 | 6152.6 | 6.73 | 4
CZ03 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2231.4 | 2231.4 | 7 | 4
CZ03 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 15105.8 | 15105.8 | 6.74 | 4
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1653.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6200.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1362.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5395 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1718.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6287.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1638.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10172.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1346.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9452.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1704.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10169.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1638.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10178.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1346.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5205.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1712.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6235.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1712.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6237.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1345.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5206 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1637.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10197.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2277.8 | 2277.8 | 6.98 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8541 | 8541 | 6.79 | 4
CZ04 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1877 | 1877 | 6.59 | 4
CZ04 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7431.1 | 7431.1 | 6.76 | 4
CZ04 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2367 | 2367 | 6.95 | 4
CZ04 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8660.9 | 8660.9 | 6.78 | 4
CZ04 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2256.8 | 2256.8 | 6.99 | 4
CZ04 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 14012.2 | 14012.2 | 6.8 | 4
CZ04 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1855.1 | 1855.1 | 6.6 | 4
CZ04 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 13020.1 | 13020.1 | 6.69 | 4
CZ04 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2347.2 | 2347.2 | 6.96 | 4
CZ04 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 14007.7 | 14007.7 | 6.8 | 4
CZ04 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2256.3 | 2256.3 | 6.99 | 4
CZ04 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 14019.6 | 14019.6 | 6.8 | 4
CZ04 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1854.1 | 1854.1 | 6.6 | 4
CZ04 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7170.2 | 7170.2 | 6.79 | 4
CZ04 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2358.6 | 2358.6 | 6.95 | 4
CZ04 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 8589 | 8589 | 6.79 | 4
CZ04 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2358.8 | 2358.8 | 6.95 | 4
CZ04 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 8591.2 | 8591.2 | 6.79 | 4
CZ04 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1853.7 | 1853.7 | 6.6 | 4
CZ04 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7170.8 | 7170.8 | 6.79 | 4
CZ04 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2255.3 | 2255.3 | 6.99 | 4
CZ04 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 14046.6 | 14046.6 | 6.8 | 4
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1706.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6074.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1066 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4963 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1764.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6038.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1715.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 11410.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1074.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 10843.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1773.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 11392.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1714.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 11104.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1066 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4505.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1756.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 7087.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1765.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 7120.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1074.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4498.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1723.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 11139.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2350.7 | 2350.7 | 6.96 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8367.1 | 8367.1 | 6.81 | 4
CZ05 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1468.3 | 1468.3 | 6.77 | 4
CZ05 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 6836.1 | 6836.1 | 6.83 | 4
CZ05 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2430.6 | 2430.6 | 6.93 | 4
CZ05 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8317.7 | 8317.7 | 6.81 | 4
CZ05 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2362.9 | 2362.9 | 6.95 | 4
CZ05 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 15716.8 | 15716.8 | 6.71 | 4
CZ05 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1480.1 | 1480.1 | 6.76 | 4
CZ05 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14936.6 | 14936.6 | 6.75 | 4
CZ05 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2442.6 | 2442.6 | 6.92 | 4
CZ05 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 15692.4 | 15692.4 | 6.71 | 4
CZ05 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2361.4 | 2361.4 | 6.95 | 4
CZ05 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 15295.7 | 15295.7 | 6.73 | 4
CZ05 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1468.3 | 1468.3 | 6.77 | 4
CZ05 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6206.2 | 6206.2 | 6.72 | 4
CZ05 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2419.3 | 2419.3 | 6.93 | 4
CZ05 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 9762.3 | 9762.3 | 6.81 | 4
CZ05 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2431.3 | 2431.3 | 6.93 | 4
CZ05 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 9807.6 | 9807.6 | 6.8 | 4
CZ05 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1480.1 | 1480.1 | 6.76 | 4
CZ05 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6196.7 | 6196.7 | 6.72 | 4
CZ05 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2373.5 | 2373.5 | 6.95 | 4
CZ05 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 15343.8 | 15343.8 | 6.73 | 4
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1748.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6427.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1211.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5579.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1789.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6006.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1735.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10553.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1198.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9900.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1776.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10572.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1734.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10347.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1198.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4447.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1783.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 7744 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1788.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 7795.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1202.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4463.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1739.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10386.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2408.8 | 2408.8 | 6.94 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8853.6 | 8853.6 | 6.76 | 4
CZ06 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1668.7 | 1668.7 | 6.67 | 4
CZ06 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7685.1 | 7685.1 | 6.73 | 4
CZ06 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2465.3 | 2465.3 | 6.92 | 4
CZ06 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8273.8 | 8273.8 | 6.82 | 4
CZ06 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2389.9 | 2389.9 | 6.94 | 4
CZ06 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 14537.1 | 14537.1 | 6.77 | 4
CZ06 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1651 | 1651 | 6.68 | 4
CZ06 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 13636.9 | 13636.9 | 6.83 | 4
CZ06 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2446.4 | 2446.4 | 6.92 | 4
CZ06 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 14563 | 14563 | 6.77 | 4
CZ06 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2389.6 | 2389.6 | 6.94 | 4
CZ06 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 14252.5 | 14252.5 | 6.79 | 4
CZ06 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1650.3 | 1650.3 | 6.68 | 4
CZ06 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6126.1 | 6126.1 | 6.73 | 4
CZ06 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2456.8 | 2456.8 | 6.92 | 4
CZ06 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 10666.6 | 10666.6 | 6.74 | 4
CZ06 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2463.8 | 2463.8 | 6.92 | 4
CZ06 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 10738.2 | 10738.2 | 6.73 | 4
CZ06 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1656.8 | 1656.8 | 6.67 | 4
CZ06 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6147.7 | 6147.7 | 6.73 | 4
CZ06 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2396.5 | 2396.5 | 6.94 | 4
CZ06 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 14306.9 | 14306.9 | 6.79 | 4
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1309.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5491 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1153.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5082.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1467.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5372.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1301.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10376.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1144.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9890.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1459.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10391.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1298.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10120.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1143.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4703.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1471.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 7144.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1466.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 7247.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1141.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4719.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1294.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10193.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 1803.2 | 1803.2 | 6.61 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 7563.3 | 7563.3 | 6.74 | 4
CZ07 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1589 | 1589 | 6.7 | 4
CZ07 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7001.1 | 7001.1 | 6.81 | 4
CZ07 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2021.5 | 2021.5 | 6.54 | 4
CZ07 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 7400.6 | 7400.6 | 6.76 | 4
CZ07 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 1793.1 | 1793.1 | 6.62 | 4
CZ07 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 14292.5 | 14292.5 | 6.79 | 4
CZ07 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1576.6 | 1576.6 | 6.71 | 4
CZ07 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 13623.6 | 13623.6 | 6.83 | 4
CZ07 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2010.8 | 2010.8 | 6.55 | 4
CZ07 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 14313.3 | 14313.3 | 6.79 | 4
CZ07 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 1789.1 | 1789.1 | 6.62 | 4
CZ07 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 13940.7 | 13940.7 | 6.81 | 4
CZ07 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1575.1 | 1575.1 | 6.71 | 4
CZ07 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6478.5 | 6478.5 | 6.69 | 4
CZ07 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2026.3 | 2026.3 | 6.54 | 4
CZ07 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 9841.1 | 9841.1 | 6.8 | 4
CZ07 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2020.3 | 2020.3 | 6.54 | 4
CZ07 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 9982.8 | 9982.8 | 6.79 | 4
CZ07 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1572.9 | 1572.9 | 6.71 | 4
CZ07 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6500.4 | 6500.4 | 6.69 | 4
CZ07 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 1783.3 | 1783.3 | 6.62 | 4
CZ07 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 14040.4 | 14040.4 | 6.8 | 4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1832.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6645 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1584.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5751.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2006.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6725.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1827.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 12342 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1579.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 11568 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1997.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 12412.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1822.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 12030 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1577.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5632.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2005.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 7966.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2004.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 8045.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1577.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5758 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1821.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 12151 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2523.7 | 2523.7 | 6.9 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 9152.9 | 9152.9 | 6.74 | 4
CZ08 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2182.5 | 2182.5 | 6.5 | 4
CZ08 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7922.1 | 7922.1 | 6.71 | 4
CZ08 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2763.3 | 2763.3 | 6.82 | 4
CZ08 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 9263.4 | 9263.4 | 6.73 | 4
CZ08 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2516.8 | 2516.8 | 6.9 | 4
CZ08 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 17000 | 17000 | 6.8 | 4
CZ08 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2175.9 | 2175.9 | 6.5 | 4
CZ08 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 15933.9 | 15933.9 | 6.7 | 4
CZ08 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2751 | 2751 | 6.82 | 4
CZ08 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 17097.1 | 17097.1 | 6.79 | 4
CZ08 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2510.8 | 2510.8 | 6.9 | 4
CZ08 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 16570.3 | 16570.3 | 6.82 | 4
CZ08 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2172.8 | 2172.8 | 6.5 | 4
CZ08 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7758.2 | 7758.2 | 6.72 | 4
CZ08 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2762.1 | 2762.1 | 6.82 | 4
CZ08 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 10973.2 | 10973.2 | 6.71 | 4
CZ08 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2761.1 | 2761.1 | 6.82 | 4
CZ08 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 11081.7 | 11081.7 | 6.81 | 4
CZ08 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2172.6 | 2172.6 | 6.5 | 4
CZ08 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7931.2 | 7931.2 | 6.71 | 4
CZ08 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2509 | 2509 | 6.9 | 4
CZ08 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 16736.9 | 16736.9 | 6.81 | 4
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2013.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 7666.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1608.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 6636.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2126.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 7738.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2007.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 13467.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1600.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 12555.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2119.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 13472.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2004.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 13297.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1599.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 6544.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2124.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 9282.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2124.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 9374 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1599.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 6546.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2004.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 13326.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2772.9 | 2772.9 | 6.81 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 10559.5 | 10559.5 | 6.74 | 4
CZ09 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2215.4 | 2215.4 | 7 | 4
CZ09 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 9141.3 | 9141.3 | 6.74 | 4
CZ09 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2929 | 2929 | 6.77 | 4
CZ09 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 10658.6 | 10658.6 | 6.74 | 4
CZ09 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2764.6 | 2764.6 | 6.82 | 4
CZ09 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 18550.4 | 18550.4 | 6.72 | 4
CZ09 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2204.4 | 2204.4 | 7.01 | 4
CZ09 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 17293.9 | 17293.9 | 6.78 | 4
CZ09 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2919.9 | 2919.9 | 6.77 | 4
CZ09 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 18557.2 | 18557.2 | 6.72 | 4
CZ09 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2761.1 | 2761.1 | 6.82 | 4
CZ09 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 18316.6 | 18316.6 | 6.73 | 4
CZ09 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2202.6 | 2202.6 | 7.01 | 4
CZ09 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 9014.2 | 9014.2 | 6.75 | 4
CZ09 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2926.1 | 2926.1 | 6.77 | 4
CZ09 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 12786.1 | 12786.1 | 6.7 | 4
CZ09 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2926.4 | 2926.4 | 6.77 | 4
CZ09 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 12911.9 | 12911.9 | 6.69 | 4
CZ09 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2202.8 | 2202.8 | 7.01 | 4
CZ09 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 9017 | 9017 | 6.75 | 4
CZ09 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2761.2 | 2761.2 | 6.82 | 4
CZ09 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 18356.2 | 18356.2 | 6.73 | 4
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2576.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 7217.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1787.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5617.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2622.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 7229.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2564.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 11838 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1775.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 10852.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2611.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 11878.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2562.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 11537.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1773.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5341.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2616.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 7145.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2616.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 7153.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1773.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5480.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2562.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 11578.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 3548.3 | 3548.3 | 6.63 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 9941 | 9941 | 6.79 | 4
CZ10 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2462.1 | 2462.1 | 6.92 | 4
CZ10 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7737.8 | 7737.8 | 6.72 | 4
CZ10 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 3612.6 | 3612.6 | 6.61 | 4
CZ10 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 9957.9 | 9957.9 | 6.79 | 4
CZ10 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 3532.4 | 3532.4 | 6.63 | 4
CZ10 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 16305.9 | 16305.9 | 6.83 | 4
CZ10 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2445.5 | 2445.5 | 6.92 | 4
CZ10 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14948.1 | 14948.1 | 6.75 | 4
CZ10 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 3596.8 | 3596.8 | 6.62 | 4
CZ10 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 16361.7 | 16361.7 | 6.83 | 4
CZ10 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 3529.4 | 3529.4 | 6.63 | 4
CZ10 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 15892 | 15892 | 6.7 | 4
CZ10 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2442.8 | 2442.8 | 6.92 | 4
CZ10 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7357.7 | 7357.7 | 6.76 | 4
CZ10 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 3604.1 | 3604.1 | 6.62 | 4
CZ10 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 9842.5 | 9842.5 | 6.8 | 4
CZ10 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 3604.5 | 3604.5 | 6.61 | 4
CZ10 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 9853.5 | 9853.5 | 6.8 | 4
CZ10 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2443.2 | 2443.2 | 6.92 | 4
CZ10 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7548.6 | 7548.6 | 6.74 | 4
CZ10 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 3529.7 | 3529.7 | 6.63 | 4
CZ10 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 15948.5 | 15948.5 | 6.7 | 4
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 3181.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 8944.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2416.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 7613.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3370.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 9203.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 3169 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 14341.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2437.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 12860.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3360.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 14365.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 3171.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 13979.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2407.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 7573.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3368.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 9564.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3365.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 9829.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2404 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 7571.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3169 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 14020.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 4381.7 | 4381.7 | 6.77 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 12319.8 | 12319.8 | 6.73 | 4
CZ11 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 3328 | 3328 | 6.67 | 4
CZ11 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 10487.3 | 10487.3 | 6.75 | 4
CZ11 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 4642.8 | 4642.8 | 6.72 | 4
CZ11 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 12677.3 | 12677.3 | 6.71 | 4
CZ11 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 4365.1 | 4365.1 | 6.77 | 4
CZ11 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 19754.2 | 19754.2 | 6.8 | 4
CZ11 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 3357.9 | 3357.9 | 6.66 | 4
CZ11 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 17713.7 | 17713.7 | 6.76 | 4
CZ11 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 4628.4 | 4628.4 | 6.73 | 4
CZ11 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 19787.8 | 19787.8 | 6.8 | 4
CZ11 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 4369 | 4369 | 6.77 | 4
CZ11 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 19256.2 | 19256.2 | 6.82 | 4
CZ11 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 3315.5 | 3315.5 | 6.67 | 4
CZ11 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 10432.2 | 10432.2 | 6.75 | 4
CZ11 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 4639.7 | 4639.7 | 6.72 | 4
CZ11 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 13173.7 | 13173.7 | 6.68 | 4
CZ11 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 4635.4 | 4635.4 | 6.73 | 4
CZ11 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 13538.8 | 13538.8 | 6.83 | 4
CZ11 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 3311.3 | 3311.3 | 6.67 | 4
CZ11 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 10428.9 | 10428.9 | 6.75 | 4
CZ11 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 4365 | 4365 | 6.77 | 4
CZ11 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 19311.9 | 19311.9 | 6.82 | 4
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1522 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5924.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1149.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4619.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1718.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5964 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1504.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9543.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1132.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 8788.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1714.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9631.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1502.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9322 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1128.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4404.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1710.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5901.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1712.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5921.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1131.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4423.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1505.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9467.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2096.4 | 2096.4 | 6.52 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8160.3 | 8160.3 | 6.83 | 4
CZ12 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1583.3 | 1583.3 | 6.71 | 4
CZ12 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 6362.6 | 6362.6 | 6.7 | 4
CZ12 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2367.5 | 2367.5 | 6.95 | 4
CZ12 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8214.8 | 8214.8 | 6.82 | 4
CZ12 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2071.8 | 2071.8 | 6.53 | 4
CZ12 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 13145.1 | 13145.1 | 6.68 | 4
CZ12 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1560 | 1560 | 6.72 | 4
CZ12 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 12105 | 12105 | 6.74 | 4
CZ12 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2361.3 | 2361.3 | 6.95 | 4
CZ12 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 13266 | 13266 | 6.85 | 4
CZ12 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2069.1 | 2069.1 | 6.53 | 4
CZ12 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 12840.3 | 12840.3 | 6.7 | 4
CZ12 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1554.2 | 1554.2 | 6.72 | 4
CZ12 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6066.7 | 6066.7 | 6.74 | 4
CZ12 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2356.3 | 2356.3 | 6.96 | 4
CZ12 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 8128.9 | 8128.9 | 6.83 | 4
CZ12 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2358.2 | 2358.2 | 6.95 | 4
CZ12 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 8155.8 | 8155.8 | 6.83 | 4
CZ12 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1558.9 | 1558.9 | 6.72 | 4
CZ12 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6092.5 | 6092.5 | 6.74 | 4
CZ12 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2073.6 | 2073.6 | 6.53 | 4
CZ12 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 13041.2 | 13041.2 | 6.69 | 4
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 4641.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 10997.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 3548.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 9068.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 4681.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 11014.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 4638 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 15353.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 3543.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 13721.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 4680.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 15357 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 4637.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 15576.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 3537.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 8952.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 4673.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 10969.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 4680.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 10987.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 3543.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 8965.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 4642.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 15719.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 6393 | 6393 | 6.7 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 15148.1 | 15148.1 | 6.74 | 4
CZ13 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 4888.2 | 4888.2 | 6.69 | 4
CZ13 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 12490.6 | 12490.6 | 6.72 | 4
CZ13 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 6448.7 | 6448.7 | 6.69 | 4
CZ13 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 15172.1 | 15172.1 | 6.74 | 4
CZ13 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 6388.4 | 6388.4 | 6.7 | 4
CZ13 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 21148.3 | 21148.3 | 6.74 | 4
CZ13 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 4881.4 | 4881.4 | 6.69 | 4
CZ13 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 18899.7 | 18899.7 | 6.71 | 4
CZ13 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 6446.5 | 6446.5 | 6.69 | 4
CZ13 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 21152.9 | 21152.9 | 6.74 | 4
CZ13 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 6387.3 | 6387.3 | 6.7 | 4
CZ13 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 21455.3 | 21455.3 | 6.73 | 4
CZ13 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 4872.9 | 4872.9 | 6.69 | 4
CZ13 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 12331.1 | 12331.1 | 6.73 | 4
CZ13 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 6437.1 | 6437.1 | 6.69 | 4
CZ13 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 15109.5 | 15109.5 | 6.74 | 4
CZ13 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 6446.9 | 6446.9 | 6.69 | 4
CZ13 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 15134.6 | 15134.6 | 6.74 | 4
CZ13 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 4880.8 | 4880.8 | 6.69 | 4
CZ13 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 12349.4 | 12349.4 | 6.73 | 4
CZ13 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 6394.9 | 6394.9 | 6.7 | 4
CZ13 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 21652.8 | 21652.8 | 6.72 | 4
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 3300.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 7822.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2149.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5865.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3362.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 7862.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 3300.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 11858.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2150.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 10540.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3362.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 11981 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 3299.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 11776.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2142.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5771.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3354.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 8096.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3361.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 8276.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2150.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5789 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3306.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 11940.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 4546.5 | 4546.5 | 6.74 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 10774.8 | 10774.8 | 6.73 | 4
CZ14 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2961.2 | 2961.2 | 6.76 | 4
CZ14 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 8078.7 | 8078.7 | 6.84 | 4
CZ14 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 4631.2 | 4631.2 | 6.73 | 4
CZ14 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 10830 | 10830 | 6.72 | 4
CZ14 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 4546.2 | 4546.2 | 6.74 | 4
CZ14 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 16334.5 | 16334.5 | 6.83 | 4
CZ14 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2962.4 | 2962.4 | 6.76 | 4
CZ14 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14518.9 | 14518.9 | 6.77 | 4
CZ14 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 4631.8 | 4631.8 | 6.73 | 4
CZ14 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 16502.8 | 16502.8 | 6.82 | 4
CZ14 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 4544.7 | 4544.7 | 6.74 | 4
CZ14 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 16221.5 | 16221.5 | 6.84 | 4
CZ14 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2951 | 2951 | 6.76 | 4
CZ14 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7949.8 | 7949.8 | 6.7 | 4
CZ14 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 4620.1 | 4620.1 | 6.73 | 4
CZ14 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 11152.5 | 11152.5 | 6.81 | 4
CZ14 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 4630.3 | 4630.3 | 6.73 | 4
CZ14 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 11400 | 11400 | 6.79 | 4
CZ14 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2961.7 | 2961.7 | 6.76 | 4
CZ14 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7973.8 | 7973.8 | 6.7 | 4
CZ14 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 4555 | 4555 | 6.74 | 4
CZ14 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 16447.6 | 16447.6 | 6.82 | 4
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 4295.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 10411 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 3276.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 8661.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 4510.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 10593.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 4290.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 16201.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 3271.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 14442.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 4505.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 16472.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 4288.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 15834 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 3271.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 8653.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 4509.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 11321.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 4510.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 11781 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 3272 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 9049.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 4288.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 16248 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 5916.9 | 5916.9 | 6.76 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 14340.3 | 14340.3 | 6.79 | 4
CZ15 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 4513 | 4513 | 6.75 | 4
CZ15 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 11930.9 | 11930.9 | 6.75 | 4
CZ15 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 6212.8 | 6212.8 | 6.72 | 4
CZ15 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 14592.2 | 14592.2 | 6.77 | 4
CZ15 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 5910.1 | 5910.1 | 6.76 | 4
CZ15 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 22316 | 22316 | 6.81 | 4
CZ15 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 4506.7 | 4506.7 | 6.75 | 4
CZ15 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 19892.8 | 19892.8 | 6.79 | 4
CZ15 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 6205.6 | 6205.6 | 6.72 | 4
CZ15 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 22689.4 | 22689.4 | 6.79 | 4
CZ15 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 5906.9 | 5906.9 | 6.76 | 4
CZ15 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 21809.9 | 21809.9 | 6.72 | 4
CZ15 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 4506.3 | 4506.3 | 6.75 | 4
CZ15 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 11919.7 | 11919.7 | 6.75 | 4
CZ15 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 6212 | 6212 | 6.72 | 4
CZ15 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 15593.9 | 15593.9 | 6.72 | 4
CZ15 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 6212.6 | 6212.6 | 6.72 | 4
CZ15 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 16227.4 | 16227.4 | 6.83 | 4
CZ15 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 4506.8 | 4506.8 | 6.75 | 4
CZ15 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 12465.2 | 12465.2 | 6.72 | 4
CZ15 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 5907.3 | 5907.3 | 6.76 | 4
CZ15 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 22380.2 | 22380.2 | 6.81 | 4
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2854.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 9253.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2092.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 7741.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2948.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 9395.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2829.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 16108.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2073.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 14767.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2930.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 16254.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2827.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 15654.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2071.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 7568.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2947.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 9370.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2939.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 9484.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2068.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 7676 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2825.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 15910.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 3931.3 | 3931.3 | 6.86 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 12745.3 | 12745.3 | 6.7 | 4
CZ16 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2882.5 | 2882.5 | 6.78 | 4
CZ16 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 10663.3 | 10663.3 | 6.74 | 4
CZ16 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 4061 | 4061 | 6.83 | 4
CZ16 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 12941.1 | 12941.1 | 6.69 | 4
CZ16 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 3897.5 | 3897.5 | 6.87 | 4
CZ16 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 22188.5 | 22188.5 | 6.81 | 4
CZ16 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2855.8 | 2855.8 | 6.79 | 4
CZ16 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 20341.2 | 20341.2 | 6.77 | 4
CZ16 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 4036.9 | 4036.9 | 6.84 | 4
CZ16 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 22389.5 | 22389.5 | 6.81 | 4
CZ16 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 3894.8 | 3894.8 | 6.87 | 4
CZ16 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 21562.4 | 21562.4 | 6.73 | 4
CZ16 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2852.7 | 2852.7 | 6.79 | 4
CZ16 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 10424.9 | 10424.9 | 6.75 | 4
CZ16 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 4059.7 | 4059.7 | 6.83 | 4
CZ16 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 12906.6 | 12906.6 | 6.69 | 4
CZ16 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 4049.2 | 4049.2 | 6.84 | 4
CZ16 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 13064.6 | 13064.6 | 6.68 | 4
CZ16 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2849.7 | 2849.7 | 6.79 | 4
CZ16 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 10573 | 10573 | 6.74 | 4
CZ16 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 3892 | 3892 | 6.87 | 4
CZ16 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 21915.6 | 21915.6 | 6.72 | 4
DX Heating Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 868.1 | 868.1 | 7.07 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 3176.1 | 3176.1 | 6.7 | 4
CZ01 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 107.1 | 107.1 | 3.9 | 4
CZ01 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 2943.1 | 2943.1 | 6.76 | 4
CZ01 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 713.1 | 713.1 | 6.91 | 4
CZ01 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 2567.3 | 2567.3 | 6.88 | 4
CZ01 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 876.4 | 876.4 | 7.07 | 4
CZ01 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 9236.6 | 9236.6 | 6.73 | 4
CZ01 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 111.6 | 111.6 | 3.93 | 4
CZ01 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 9204.3 | 9204.3 | 6.73 | 4
CZ01 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 717.4 | 717.4 | 6.92 | 4
CZ01 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 9217 | 9217 | 6.73 | 4
CZ01 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 875.1 | 875.1 | 7.07 | 4
CZ01 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 9286.4 | 9286.4 | 6.72 | 4
CZ01 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 107.1 | 107.1 | 3.9 | 4
CZ01 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 1716.2 | 1716.2 | 6.65 | 4
CZ01 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 705.7 | 705.7 | 6.88 | 4
CZ01 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 5166.2 | 5166.2 | 6.87 | 4
CZ01 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 709.9 | 709.9 | 6.9 | 4
CZ01 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 5238.9 | 5238.9 | 6.86 | 4
CZ01 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 111.6 | 111.6 | 3.93 | 4
CZ01 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 1723.1 | 1723.1 | 6.65 | 4
CZ01 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 883.4 | 883.4 | 7.08 | 4
CZ01 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 9294.5 | 9294.5 | 6.72 | 4
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2047.5 | 2047.5 | 6.54 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8290.9 | 8290.9 | 6.82 | 4
CZ02 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1691.8 | 1691.8 | 6.66 | 4
CZ02 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7166.5 | 7166.5 | 6.79 | 4
CZ02 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2140.6 | 2140.6 | 6.51 | 4
CZ02 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8344.1 | 8344.1 | 6.81 | 4
CZ02 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2019.4 | 2019.4 | 6.54 | 4
CZ02 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 13706.5 | 13706.5 | 6.82 | 4
CZ02 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1660.3 | 1660.3 | 6.67 | 4
CZ02 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 12783.8 | 12783.8 | 6.7 | 4
CZ02 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2111.9 | 2111.9 | 6.52 | 4
CZ02 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 13720.9 | 13720.9 | 6.82 | 4
CZ02 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2017.2 | 2017.2 | 6.54 | 4
CZ02 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 13701 | 13701 | 6.82 | 4
CZ02 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1658.2 | 1658.2 | 6.67 | 4
CZ02 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6787.2 | 6787.2 | 6.83 | 4
CZ02 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2126.8 | 2126.8 | 6.51 | 4
CZ02 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 8204 | 8204 | 6.83 | 4
CZ02 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2129 | 2129 | 6.51 | 4
CZ02 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 8222.5 | 8222.5 | 6.82 | 4
CZ02 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1660.2 | 1660.2 | 6.67 | 4
CZ02 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6798.8 | 6798.8 | 6.83 | 4
CZ02 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2018.6 | 2018.6 | 6.54 | 4
CZ02 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 13735 | 13735 | 6.82 | 4
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2266.8 | 2266.8 | 6.99 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 9053.5 | 9053.5 | 6.74 | 4
CZ03 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1578.2 | 1578.2 | 6.71 | 4
CZ03 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7765.8 | 7765.8 | 6.72 | 4
CZ03 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2309.1 | 2309.1 | 6.97 | 4
CZ03 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8361.3 | 8361.3 | 6.81 | 4
CZ03 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2239.9 | 2239.9 | 7 | 4
CZ03 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 15393.5 | 15393.5 | 6.73 | 4
CZ03 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1553.4 | 1553.4 | 6.72 | 4
CZ03 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14477.9 | 14477.9 | 6.78 | 4
CZ03 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2282.7 | 2282.7 | 6.98 | 4
CZ03 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 15401 | 15401 | 6.73 | 4
CZ03 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2240.8 | 2240.8 | 7 | 4
CZ03 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 15088.4 | 15088.4 | 6.74 | 4
CZ03 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1561.5 | 1561.5 | 6.72 | 4
CZ03 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6170.1 | 6170.1 | 6.73 | 4
CZ03 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2314 | 2314 | 6.97 | 4
CZ03 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 11013.3 | 11013.3 | 6.82 | 4
CZ03 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2304.2 | 2304.2 | 6.97 | 4
CZ03 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 11003.8 | 11003.8 | 6.82 | 4
CZ03 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1552.7 | 1552.7 | 6.72 | 4
CZ03 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6152.6 | 6152.6 | 6.73 | 4
CZ03 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2231.4 | 2231.4 | 7 | 4
CZ03 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 15105.8 | 15105.8 | 6.74 | 4
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2277.8 | 2277.8 | 6.98 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8541 | 8541 | 6.79 | 4
CZ04 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1877 | 1877 | 6.59 | 4
CZ04 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7431.1 | 7431.1 | 6.76 | 4
CZ04 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2367 | 2367 | 6.95 | 4
CZ04 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8660.9 | 8660.9 | 6.78 | 4
CZ04 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2256.8 | 2256.8 | 6.99 | 4
CZ04 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 14012.2 | 14012.2 | 6.8 | 4
CZ04 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1855.1 | 1855.1 | 6.6 | 4
CZ04 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 13020.1 | 13020.1 | 6.69 | 4
CZ04 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2347.2 | 2347.2 | 6.96 | 4
CZ04 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 14007.7 | 14007.7 | 6.8 | 4
CZ04 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2256.3 | 2256.3 | 6.99 | 4
CZ04 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 14019.6 | 14019.6 | 6.8 | 4
CZ04 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1854.1 | 1854.1 | 6.6 | 4
CZ04 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7170.2 | 7170.2 | 6.79 | 4
CZ04 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2358.6 | 2358.6 | 6.95 | 4
CZ04 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 8589 | 8589 | 6.79 | 4
CZ04 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2358.8 | 2358.8 | 6.95 | 4
CZ04 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 8591.2 | 8591.2 | 6.79 | 4
CZ04 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1853.7 | 1853.7 | 6.6 | 4
CZ04 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7170.8 | 7170.8 | 6.79 | 4
CZ04 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2255.3 | 2255.3 | 6.99 | 4
CZ04 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 14046.6 | 14046.6 | 6.8 | 4
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2350.7 | 2350.7 | 6.96 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8367.1 | 8367.1 | 6.81 | 4
CZ05 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1468.3 | 1468.3 | 6.77 | 4
CZ05 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 6836.1 | 6836.1 | 6.83 | 4
CZ05 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2430.6 | 2430.6 | 6.93 | 4
CZ05 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8317.7 | 8317.7 | 6.81 | 4
CZ05 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2362.9 | 2362.9 | 6.95 | 4
CZ05 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 15716.8 | 15716.8 | 6.71 | 4
CZ05 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1480.1 | 1480.1 | 6.76 | 4
CZ05 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14936.6 | 14936.6 | 6.75 | 4
CZ05 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2442.6 | 2442.6 | 6.92 | 4
CZ05 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 15692.4 | 15692.4 | 6.71 | 4
CZ05 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2361.4 | 2361.4 | 6.95 | 4
CZ05 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 15295.7 | 15295.7 | 6.73 | 4
CZ05 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1468.3 | 1468.3 | 6.77 | 4
CZ05 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6206.2 | 6206.2 | 6.72 | 4
CZ05 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2419.3 | 2419.3 | 6.93 | 4
CZ05 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 9762.3 | 9762.3 | 6.81 | 4
CZ05 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2431.3 | 2431.3 | 6.93 | 4
CZ05 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 9807.6 | 9807.6 | 6.8 | 4
CZ05 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1480.1 | 1480.1 | 6.76 | 4
CZ05 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6196.7 | 6196.7 | 6.72 | 4
CZ05 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2373.5 | 2373.5 | 6.95 | 4
CZ05 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 15343.8 | 15343.8 | 6.73 | 4
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2408.8 | 2408.8 | 6.94 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8853.6 | 8853.6 | 6.76 | 4
CZ06 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1668.7 | 1668.7 | 6.67 | 4
CZ06 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7685.1 | 7685.1 | 6.73 | 4
CZ06 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2465.3 | 2465.3 | 6.92 | 4
CZ06 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8273.8 | 8273.8 | 6.82 | 4
CZ06 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2389.9 | 2389.9 | 6.94 | 4
CZ06 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 14537.1 | 14537.1 | 6.77 | 4
CZ06 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1651 | 1651 | 6.68 | 4
CZ06 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 13636.9 | 13636.9 | 6.83 | 4
CZ06 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2446.4 | 2446.4 | 6.92 | 4
CZ06 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 14563 | 14563 | 6.77 | 4
CZ06 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2389.6 | 2389.6 | 6.94 | 4
CZ06 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 14252.5 | 14252.5 | 6.79 | 4
CZ06 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1650.3 | 1650.3 | 6.68 | 4
CZ06 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6126.1 | 6126.1 | 6.73 | 4
CZ06 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2456.8 | 2456.8 | 6.92 | 4
CZ06 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 10666.6 | 10666.6 | 6.74 | 4
CZ06 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2463.8 | 2463.8 | 6.92 | 4
CZ06 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 10738.2 | 10738.2 | 6.73 | 4
CZ06 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1656.8 | 1656.8 | 6.67 | 4
CZ06 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6147.7 | 6147.7 | 6.73 | 4
CZ06 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2396.5 | 2396.5 | 6.94 | 4
CZ06 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 14306.9 | 14306.9 | 6.79 | 4
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 1803.2 | 1803.2 | 6.61 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 7563.3 | 7563.3 | 6.74 | 4
CZ07 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1589 | 1589 | 6.7 | 4
CZ07 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7001.1 | 7001.1 | 6.81 | 4
CZ07 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2021.5 | 2021.5 | 6.54 | 4
CZ07 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 7400.6 | 7400.6 | 6.76 | 4
CZ07 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 1793.1 | 1793.1 | 6.62 | 4
CZ07 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 14292.5 | 14292.5 | 6.79 | 4
CZ07 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1576.6 | 1576.6 | 6.71 | 4
CZ07 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 13623.6 | 13623.6 | 6.83 | 4
CZ07 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2010.8 | 2010.8 | 6.55 | 4
CZ07 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 14313.3 | 14313.3 | 6.79 | 4
CZ07 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 1789.1 | 1789.1 | 6.62 | 4
CZ07 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 13940.7 | 13940.7 | 6.81 | 4
CZ07 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1575.1 | 1575.1 | 6.71 | 4
CZ07 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6478.5 | 6478.5 | 6.69 | 4
CZ07 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2026.3 | 2026.3 | 6.54 | 4
CZ07 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 9841.1 | 9841.1 | 6.8 | 4
CZ07 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2020.3 | 2020.3 | 6.54 | 4
CZ07 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 9982.8 | 9982.8 | 6.79 | 4
CZ07 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1572.9 | 1572.9 | 6.71 | 4
CZ07 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6500.4 | 6500.4 | 6.69 | 4
CZ07 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 1783.3 | 1783.3 | 6.62 | 4
CZ07 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 14040.4 | 14040.4 | 6.8 | 4
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2523.7 | 2523.7 | 6.9 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 9152.9 | 9152.9 | 6.74 | 4
CZ08 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2182.5 | 2182.5 | 6.5 | 4
CZ08 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7922.1 | 7922.1 | 6.71 | 4
CZ08 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2763.3 | 2763.3 | 6.82 | 4
CZ08 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 9263.4 | 9263.4 | 6.73 | 4
CZ08 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2516.8 | 2516.8 | 6.9 | 4
CZ08 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 17000 | 17000 | 6.8 | 4
CZ08 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2175.9 | 2175.9 | 6.5 | 4
CZ08 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 15933.9 | 15933.9 | 6.7 | 4
CZ08 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2751 | 2751 | 6.82 | 4
CZ08 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 17097.1 | 17097.1 | 6.79 | 4
CZ08 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2510.8 | 2510.8 | 6.9 | 4
CZ08 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 16570.3 | 16570.3 | 6.82 | 4
CZ08 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2172.8 | 2172.8 | 6.5 | 4
CZ08 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7758.2 | 7758.2 | 6.72 | 4
CZ08 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2762.1 | 2762.1 | 6.82 | 4
CZ08 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 10973.2 | 10973.2 | 6.71 | 4
CZ08 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2761.1 | 2761.1 | 6.82 | 4
CZ08 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 11081.7 | 11081.7 | 6.81 | 4
CZ08 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2172.6 | 2172.6 | 6.5 | 4
CZ08 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7931.2 | 7931.2 | 6.71 | 4
CZ08 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2509 | 2509 | 6.9 | 4
CZ08 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 16736.9 | 16736.9 | 6.81 | 4
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2772.9 | 2772.9 | 6.81 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 10559.5 | 10559.5 | 6.74 | 4
CZ09 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2215.4 | 2215.4 | 7 | 4
CZ09 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 9141.3 | 9141.3 | 6.74 | 4
CZ09 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2929 | 2929 | 6.77 | 4
CZ09 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 10658.6 | 10658.6 | 6.74 | 4
CZ09 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2764.6 | 2764.6 | 6.82 | 4
CZ09 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 18550.4 | 18550.4 | 6.72 | 4
CZ09 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2204.4 | 2204.4 | 7.01 | 4
CZ09 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 17293.9 | 17293.9 | 6.78 | 4
CZ09 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2919.9 | 2919.9 | 6.77 | 4
CZ09 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 18557.2 | 18557.2 | 6.72 | 4
CZ09 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2761.1 | 2761.1 | 6.82 | 4
CZ09 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 18316.6 | 18316.6 | 6.73 | 4
CZ09 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2202.6 | 2202.6 | 7.01 | 4
CZ09 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 9014.2 | 9014.2 | 6.75 | 4
CZ09 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2926.1 | 2926.1 | 6.77 | 4
CZ09 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 12786.1 | 12786.1 | 6.7 | 4
CZ09 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2926.4 | 2926.4 | 6.77 | 4
CZ09 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 12911.9 | 12911.9 | 6.69 | 4
CZ09 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2202.8 | 2202.8 | 7.01 | 4
CZ09 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 9017 | 9017 | 6.75 | 4
CZ09 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2761.2 | 2761.2 | 6.82 | 4
CZ09 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 18356.2 | 18356.2 | 6.73 | 4
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 3548.3 | 3548.3 | 6.63 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 9941 | 9941 | 6.79 | 4
CZ10 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2462.1 | 2462.1 | 6.92 | 4
CZ10 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 7737.8 | 7737.8 | 6.72 | 4
CZ10 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 3612.6 | 3612.6 | 6.61 | 4
CZ10 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 9957.9 | 9957.9 | 6.79 | 4
CZ10 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 3532.4 | 3532.4 | 6.63 | 4
CZ10 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 16305.9 | 16305.9 | 6.83 | 4
CZ10 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2445.5 | 2445.5 | 6.92 | 4
CZ10 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14948.1 | 14948.1 | 6.75 | 4
CZ10 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 3596.8 | 3596.8 | 6.62 | 4
CZ10 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 16361.7 | 16361.7 | 6.83 | 4
CZ10 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 3529.4 | 3529.4 | 6.63 | 4
CZ10 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 15892 | 15892 | 6.7 | 4
CZ10 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2442.8 | 2442.8 | 6.92 | 4
CZ10 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7357.7 | 7357.7 | 6.76 | 4
CZ10 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 3604.1 | 3604.1 | 6.62 | 4
CZ10 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 9842.5 | 9842.5 | 6.8 | 4
CZ10 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 3604.5 | 3604.5 | 6.61 | 4
CZ10 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 9853.5 | 9853.5 | 6.8 | 4
CZ10 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2443.2 | 2443.2 | 6.92 | 4
CZ10 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7548.6 | 7548.6 | 6.74 | 4
CZ10 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 3529.7 | 3529.7 | 6.63 | 4
CZ10 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 15948.5 | 15948.5 | 6.7 | 4
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 4381.7 | 4381.7 | 6.77 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 12319.8 | 12319.8 | 6.73 | 4
CZ11 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 3328 | 3328 | 6.67 | 4
CZ11 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 10487.3 | 10487.3 | 6.75 | 4
CZ11 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 4642.8 | 4642.8 | 6.72 | 4
CZ11 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 12677.3 | 12677.3 | 6.71 | 4
CZ11 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 4365.1 | 4365.1 | 6.77 | 4
CZ11 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 19754.2 | 19754.2 | 6.8 | 4
CZ11 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 3357.9 | 3357.9 | 6.66 | 4
CZ11 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 17713.7 | 17713.7 | 6.76 | 4
CZ11 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 4628.4 | 4628.4 | 6.73 | 4
CZ11 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 19787.8 | 19787.8 | 6.8 | 4
CZ11 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 4369 | 4369 | 6.77 | 4
CZ11 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 19256.2 | 19256.2 | 6.82 | 4
CZ11 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 3315.5 | 3315.5 | 6.67 | 4
CZ11 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 10432.2 | 10432.2 | 6.75 | 4
CZ11 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 4639.7 | 4639.7 | 6.72 | 4
CZ11 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 13173.7 | 13173.7 | 6.68 | 4
CZ11 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 4635.4 | 4635.4 | 6.73 | 4
CZ11 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 13538.8 | 13538.8 | 6.83 | 4
CZ11 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 3311.3 | 3311.3 | 6.67 | 4
CZ11 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 10428.9 | 10428.9 | 6.75 | 4
CZ11 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 4365 | 4365 | 6.77 | 4
CZ11 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 19311.9 | 19311.9 | 6.82 | 4
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 2096.4 | 2096.4 | 6.52 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 8160.3 | 8160.3 | 6.83 | 4
CZ12 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 1583.3 | 1583.3 | 6.71 | 4
CZ12 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 6362.6 | 6362.6 | 6.7 | 4
CZ12 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 2367.5 | 2367.5 | 6.95 | 4
CZ12 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 8214.8 | 8214.8 | 6.82 | 4
CZ12 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 2071.8 | 2071.8 | 6.53 | 4
CZ12 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 13145.1 | 13145.1 | 6.68 | 4
CZ12 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 1560 | 1560 | 6.72 | 4
CZ12 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 12105 | 12105 | 6.74 | 4
CZ12 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 2361.3 | 2361.3 | 6.95 | 4
CZ12 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 13266 | 13266 | 6.85 | 4
CZ12 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 2069.1 | 2069.1 | 6.53 | 4
CZ12 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 12840.3 | 12840.3 | 6.7 | 4
CZ12 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 1554.2 | 1554.2 | 6.72 | 4
CZ12 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 6066.7 | 6066.7 | 6.74 | 4
CZ12 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 2356.3 | 2356.3 | 6.96 | 4
CZ12 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 8128.9 | 8128.9 | 6.83 | 4
CZ12 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 2358.2 | 2358.2 | 6.95 | 4
CZ12 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 8155.8 | 8155.8 | 6.83 | 4
CZ12 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 1558.9 | 1558.9 | 6.72 | 4
CZ12 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 6092.5 | 6092.5 | 6.74 | 4
CZ12 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 2073.6 | 2073.6 | 6.53 | 4
CZ12 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 13041.2 | 13041.2 | 6.69 | 4
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 6393 | 6393 | 6.7 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 15148.1 | 15148.1 | 6.74 | 4
CZ13 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 4888.2 | 4888.2 | 6.69 | 4
CZ13 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 12490.6 | 12490.6 | 6.72 | 4
CZ13 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 6448.7 | 6448.7 | 6.69 | 4
CZ13 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 15172.1 | 15172.1 | 6.74 | 4
CZ13 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 6388.4 | 6388.4 | 6.7 | 4
CZ13 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 21148.3 | 21148.3 | 6.74 | 4
CZ13 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 4881.4 | 4881.4 | 6.69 | 4
CZ13 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 18899.7 | 18899.7 | 6.71 | 4
CZ13 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 6446.5 | 6446.5 | 6.69 | 4
CZ13 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 21152.9 | 21152.9 | 6.74 | 4
CZ13 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 6387.3 | 6387.3 | 6.7 | 4
CZ13 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 21455.3 | 21455.3 | 6.73 | 4
CZ13 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 4872.9 | 4872.9 | 6.69 | 4
CZ13 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 12331.1 | 12331.1 | 6.73 | 4
CZ13 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 6437.1 | 6437.1 | 6.69 | 4
CZ13 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 15109.5 | 15109.5 | 6.74 | 4
CZ13 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 6446.9 | 6446.9 | 6.69 | 4
CZ13 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 15134.6 | 15134.6 | 6.74 | 4
CZ13 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 4880.8 | 4880.8 | 6.69 | 4
CZ13 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 12349.4 | 12349.4 | 6.73 | 4
CZ13 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 6394.9 | 6394.9 | 6.7 | 4
CZ13 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 21652.8 | 21652.8 | 6.72 | 4
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 4546.5 | 4546.5 | 6.74 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 10774.8 | 10774.8 | 6.73 | 4
CZ14 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2961.2 | 2961.2 | 6.76 | 4
CZ14 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 8078.7 | 8078.7 | 6.84 | 4
CZ14 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 4631.2 | 4631.2 | 6.73 | 4
CZ14 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 10830 | 10830 | 6.72 | 4
CZ14 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 4546.2 | 4546.2 | 6.74 | 4
CZ14 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 16334.5 | 16334.5 | 6.83 | 4
CZ14 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2962.4 | 2962.4 | 6.76 | 4
CZ14 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 14518.9 | 14518.9 | 6.77 | 4
CZ14 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 4631.8 | 4631.8 | 6.73 | 4
CZ14 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 16502.8 | 16502.8 | 6.82 | 4
CZ14 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 4544.7 | 4544.7 | 6.74 | 4
CZ14 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 16221.5 | 16221.5 | 6.84 | 4
CZ14 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2951 | 2951 | 6.76 | 4
CZ14 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 7949.8 | 7949.8 | 6.7 | 4
CZ14 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 4620.1 | 4620.1 | 6.73 | 4
CZ14 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 11152.5 | 11152.5 | 6.81 | 4
CZ14 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 4630.3 | 4630.3 | 6.73 | 4
CZ14 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 11400 | 11400 | 6.79 | 4
CZ14 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2961.7 | 2961.7 | 6.76 | 4
CZ14 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 7973.8 | 7973.8 | 6.7 | 4
CZ14 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 4555 | 4555 | 6.74 | 4
CZ14 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 16447.6 | 16447.6 | 6.82 | 4
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 5916.9 | 5916.9 | 6.76 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 14340.3 | 14340.3 | 6.79 | 4
CZ15 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 4513 | 4513 | 6.75 | 4
CZ15 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 11930.9 | 11930.9 | 6.75 | 4
CZ15 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 6212.8 | 6212.8 | 6.72 | 4
CZ15 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 14592.2 | 14592.2 | 6.77 | 4
CZ15 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 5910.1 | 5910.1 | 6.76 | 4
CZ15 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 22316 | 22316 | 6.81 | 4
CZ15 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 4506.7 | 4506.7 | 6.75 | 4
CZ15 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 19892.8 | 19892.8 | 6.79 | 4
CZ15 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 6205.6 | 6205.6 | 6.72 | 4
CZ15 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 22689.4 | 22689.4 | 6.79 | 4
CZ15 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 5906.9 | 5906.9 | 6.76 | 4
CZ15 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 21809.9 | 21809.9 | 6.72 | 4
CZ15 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 4506.3 | 4506.3 | 6.75 | 4
CZ15 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 11919.7 | 11919.7 | 6.75 | 4
CZ15 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 6212 | 6212 | 6.72 | 4
CZ15 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 15593.9 | 15593.9 | 6.72 | 4
CZ15 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 6212.6 | 6212.6 | 6.72 | 4
CZ15 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 16227.4 | 16227.4 | 6.83 | 4
CZ15 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 4506.8 | 4506.8 | 6.75 | 4
CZ15 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 12465.2 | 12465.2 | 6.72 | 4
CZ15 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 5907.3 | 5907.3 | 6.76 | 4
CZ15 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 22380.2 | 22380.2 | 6.81 | 4
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSE1 HEATING COIL | 3931.3 | 3931.3 | 6.86 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSE27 HEATING COIL | 12745.3 | 12745.3 | 6.7 | 4
CZ16 | 3 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E3 HEATING COIL | 2882.5 | 2882.5 | 6.78 | 4
CZ16 | 4 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E29 HEATING COIL | 10663.3 | 10663.3 | 6.74 | 4
CZ16 | 5 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_E5 HEATING COIL | 4061 | 4061 | 6.83 | 4
CZ16 | 6 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_E31 HEATING COIL | 12941.1 | 12941.1 | 6.69 | 4
CZ16 | 7 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_SSW7 HEATING COIL | 3897.5 | 3897.5 | 6.87 | 4
CZ16 | 8 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_SSW33 HEATING COIL | 22188.5 | 22188.5 | 6.81 | 4
CZ16 | 9 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W9 HEATING COIL | 2855.8 | 2855.8 | 6.79 | 4
CZ16 | 10 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W35 HEATING COIL | 20341.2 | 20341.2 | 6.77 | 4
CZ16 | 11 | Coil:Heating:DX:SingleSpeed | DXFG EL1 G_W11 HEATING COIL | 4036.9 | 4036.9 | 6.84 | 4
CZ16 | 12 | Coil:Heating:DX:SingleSpeed | DXFG EL1 T_W37 HEATING COIL | 22389.5 | 22389.5 | 6.81 | 4
CZ16 | 13 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WSW1 HEATING COIL | 3894.8 | 3894.8 | 6.87 | 4
CZ16 | 14 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WSW27 HEATING COIL | 21562.4 | 21562.4 | 6.73 | 4
CZ16 | 15 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S3 HEATING COIL | 2852.7 | 2852.7 | 6.79 | 4
CZ16 | 16 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S29 HEATING COIL | 10424.9 | 10424.9 | 6.75 | 4
CZ16 | 17 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_S5 HEATING COIL | 4059.7 | 4059.7 | 6.83 | 4
CZ16 | 18 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_S31 HEATING COIL | 12906.6 | 12906.6 | 6.69 | 4
CZ16 | 19 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N11 HEATING COIL | 4049.2 | 4049.2 | 6.84 | 4
CZ16 | 20 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N37 HEATING COIL | 13064.6 | 13064.6 | 6.68 | 4
CZ16 | 21 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_N9 HEATING COIL | 2849.7 | 2849.7 | 6.79 | 4
CZ16 | 22 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_N35 HEATING COIL | 10573 | 10573 | 6.74 | 4
CZ16 | 23 | Coil:Heating:DX:SingleSpeed | DXFG EL2 G_WNW7 HEATING COIL | 3892 | 3892 | 6.87 | 4
CZ16 | 24 | Coil:Heating:DX:SingleSpeed | DXFG EL2 T_WNW33 HEATING COIL | 21915.6 | 21915.6 | 6.72 | 4
SWHC049-03 SEER Rated AC HP_MFm_Ex | MFm&0&rDXGF&Ex&dxAC_equip | dxAC-Res-SEER-13.0
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1099.1 | 0.0264 | 0.0264 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 1473.72 | 0.0959 | 0.0959 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3041.93 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 135.57 | 0.00326 | 0.00326 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 1376.08 | 0.0896 | 0.0896 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2172.84 | 0.0522 | 0.0522 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 902.87 | 0.0217 | 0.0217 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 1095.24 | 0.0713 | 0.0713 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3112.59 | 0.0748 | 0.0748 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1109.59 | 0.0267 | 0.0267 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 4318.65 | 0.28116 | 0.28116 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3050.38 | 0.0733 | 0.0733 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 141.24 | 0.0034 | 0.0034 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 4303.58 | 0.28018 | 0.28018 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2181.46 | 0.0524 | 0.0524 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 908.23 | 0.0218 | 0.0218 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 4309.5 | 0.28056 | 0.28056 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3118.64 | 0.075 | 0.075 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1107.96 | 0.0266 | 0.0266 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 4148.96 | 0.27011 | 0.27011 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3048.89 | 0.0733 | 0.0733 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 135.58 | 0.00326 | 0.00326 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 398.22 | 0.0259 | 0.0259 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2172.82 | 0.0522 | 0.0522 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 893.4 | 0.0215 | 0.0215 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 2275.33 | 0.14813 | 0.14813 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3102.56 | 0.0746 | 0.0746 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 898.79 | 0.0216 | 0.0216 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 2301.52 | 0.14984 | 0.14984 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3112.96 | 0.0748 | 0.0748 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 141.25 | 0.0034 | 0.0034 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 384.73 | 0.025 | 0.025 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2181.54 | 0.0525 | 0.0525 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1118.45 | 0.0269 | 0.0269 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 4145.71 | 0.2699 | 0.2699 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3057.34 | 0.0735 | 0.0735 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ02 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1086.35 | 0.0623 | 0.0623 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 236.6 | 0.00653 | 0.00653 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4354.14 | 0.25238 | 0.25238 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4674 | 0.12877 | 0.12877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 879.28 | 0.0515 | 0.0515 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3725.8 | 0.21815 | 0.21815 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3443.86 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1131.11 | 0.0652 | 0.0652 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 609.11 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4403.69 | 0.25399 | 0.25399 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4642.6 | 0.12774 | 0.12774 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1071.46 | 0.0615 | 0.0615 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 236.6 | 0.00653 | 0.00653 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7110.44 | 0.41722 | 0.41722 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4673.99 | 0.12877 | 0.12877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 862.9 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6631.78 | 0.38914 | 0.38914 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3443.77 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1115.98 | 0.0643 | 0.0643 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 609.1 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7117.92 | 0.41766 | 0.41766 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4639.92 | 0.12767 | 0.12767 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1070.32 | 0.0614 | 0.0614 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 231.05 | 0.00638 | 0.00638 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7110.83 | 0.41706 | 0.41706 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4676.62 | 0.12884 | 0.12884 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 861.8 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3528.63 | 0.2066 | 0.2066 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3459.76 | 0.0953 | 0.0953 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1123.95 | 0.0647 | 0.0647 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 615.44 | 0.017 | 0.017 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4331.08 | 0.24973 | 0.24973 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4655.41 | 0.12809 | 0.12809 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1125.09 | 0.0648 | 0.0648 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 609.14 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4340.86 | 0.25029 | 0.25029 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4642.59 | 0.12774 | 0.12774 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 862.86 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3534.62 | 0.20695 | 0.20695 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3443.95 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1071.04 | 0.0614 | 0.0614 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 213.61 | 0.0059 | 0.0059 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7128.45 | 0.41809 | 0.41809 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4661.27 | 0.12842 | 0.12842 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ03 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 989.76 | 0.069 | 0.069 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2087.07 | 0.057 | 0.057 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3953.05 | 0.27559 | 0.27559 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3812.15 | 0.10449 | 0.10449 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 689.11 | 0.048 | 0.048 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1316.48 | 0.036 | 0.036 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3390.81 | 0.23639 | 0.23639 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2814.11 | 0.0772 | 0.0772 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1008.25 | 0.0703 | 0.0703 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2208.84 | 0.0607 | 0.0607 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3650.84 | 0.25452 | 0.25452 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3925.96 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 978.03 | 0.0682 | 0.0682 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2094.25 | 0.0572 | 0.0572 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 6721.41 | 0.46858 | 0.46858 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3814.53 | 0.10456 | 0.10456 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 678.26 | 0.0473 | 0.0473 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1323.29 | 0.0362 | 0.0362 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6321.6 | 0.4407 | 0.4407 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2816.45 | 0.0773 | 0.0773 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 996.71 | 0.0695 | 0.0695 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2215.8 | 0.0608 | 0.0608 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 6724.7 | 0.46881 | 0.46881 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3926.08 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 978.43 | 0.0682 | 0.0682 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2094.25 | 0.0572 | 0.0572 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6588.19 | 0.45929 | 0.45929 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3814.48 | 0.10456 | 0.10456 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 681.81 | 0.0475 | 0.0475 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1323.29 | 0.0362 | 0.0362 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2694.1 | 0.18782 | 0.18782 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2816.49 | 0.0773 | 0.0773 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1010.39 | 0.0704 | 0.0704 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2215.8 | 0.0608 | 0.0608 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4808.75 | 0.33525 | 0.33525 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3926.26 | 0.10795 | 0.10795 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1006.08 | 0.0701 | 0.0701 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2208.84 | 0.0607 | 0.0607 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4804.58 | 0.33495 | 0.33495 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3925.78 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 677.96 | 0.0473 | 0.0473 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1316.48 | 0.036 | 0.036 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2686.44 | 0.18728 | 0.18728 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2814.11 | 0.0772 | 0.0772 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 974.3 | 0.0679 | 0.0679 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2087.07 | 0.057 | 0.057 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6595.78 | 0.45982 | 0.45982 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3812.2 | 0.1045 | 0.1045 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ04 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1208.79 | 0.0693 | 0.0693 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 235.9 | 0.00676 | 0.00676 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4531.08 | 0.25999 | 0.25999 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3684.55 | 0.10557 | 0.10557 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 975.81 | 0.0571 | 0.0571 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3864.33 | 0.2262 | 0.2262 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2617.1 | 0.075 | 0.075 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1251.14 | 0.0721 | 0.0721 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 472.56 | 0.0135 | 0.0135 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4572.1 | 0.26364 | 0.26364 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3676.69 | 0.10535 | 0.10535 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1197.67 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 251.75 | 0.00722 | 0.00722 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7270.74 | 0.42653 | 0.42653 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3698.42 | 0.10597 | 0.10597 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 964.41 | 0.0565 | 0.0565 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6755.96 | 0.39633 | 0.39633 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2630.99 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1240.69 | 0.0714 | 0.0714 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 479.07 | 0.0137 | 0.0137 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7268.42 | 0.42639 | 0.42639 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3687.9 | 0.10567 | 0.10567 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1197.43 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 258.07 | 0.0074 | 0.0074 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7278.03 | 0.42676 | 0.42676 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3696.66 | 0.10592 | 0.10592 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 963.89 | 0.0564 | 0.0564 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3728.62 | 0.21826 | 0.21826 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2617.12 | 0.075 | 0.075 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1246.77 | 0.0718 | 0.0718 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 461.89 | 0.0132 | 0.0132 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4535.27 | 0.26145 | 0.26145 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3663.54 | 0.10497 | 0.10497 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1246.85 | 0.0718 | 0.0718 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 468.42 | 0.0134 | 0.0134 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4536.45 | 0.26151 | 0.26151 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3679.22 | 0.10542 | 0.10542 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 963.68 | 0.0564 | 0.0564 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3728.96 | 0.21828 | 0.21828 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2631.13 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1196.9 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 274.09 | 0.00785 | 0.00785 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7292.01 | 0.42758 | 0.42758 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3710.51 | 0.10631 | 0.10631 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ05 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 707.96 | 0.0474 | 0.0474 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2575.92 | 0.0716 | 0.0716 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3801.71 | 0.25469 | 0.25469 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4738.24 | 0.13162 | 0.13162 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 523.38 | 0.0351 | 0.0351 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1608.95 | 0.0447 | 0.0447 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3106.07 | 0.20809 | 0.20809 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3525.27 | 0.0979 | 0.0979 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 751.71 | 0.0504 | 0.0504 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2663.48 | 0.074 | 0.074 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3779.26 | 0.25319 | 0.25319 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4810.85 | 0.13364 | 0.13364 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 690.9 | 0.0463 | 0.0463 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2589.25 | 0.0719 | 0.0719 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7141.09 | 0.47842 | 0.47842 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4748.88 | 0.13192 | 0.13192 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 507.86 | 0.034 | 0.034 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1621.84 | 0.0451 | 0.0451 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6786.57 | 0.45467 | 0.45467 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3536.34 | 0.0982 | 0.0982 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 734.74 | 0.0492 | 0.0492 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2676.6 | 0.0744 | 0.0744 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7130 | 0.47768 | 0.47768 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4819.24 | 0.13388 | 0.13388 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 690.09 | 0.0462 | 0.0462 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2587.6 | 0.0719 | 0.0719 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6949.77 | 0.4656 | 0.4656 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4746.61 | 0.13185 | 0.13185 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 507.96 | 0.034 | 0.034 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1608.96 | 0.0447 | 0.0447 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2819.86 | 0.18892 | 0.18892 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3525.24 | 0.0979 | 0.0979 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 750.03 | 0.0502 | 0.0502 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2651.08 | 0.0736 | 0.0736 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4435.71 | 0.29716 | 0.29716 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4798.91 | 0.13331 | 0.13331 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 748.27 | 0.0501 | 0.0501 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2664.22 | 0.074 | 0.074 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4456.27 | 0.29854 | 0.29854 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4811.81 | 0.13367 | 0.13367 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 506.45 | 0.0339 | 0.0339 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1621.84 | 0.0451 | 0.0451 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2815.55 | 0.18863 | 0.18863 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3536.43 | 0.0982 | 0.0982 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 688.32 | 0.0461 | 0.0461 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2600.93 | 0.0723 | 0.0723 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6971.6 | 0.46706 | 0.46706 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4756.8 | 0.13214 | 0.13214 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ06 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1140.07 | 0.0733 | 0.0733 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1579.43 | 0.044 | 0.044 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4190.29 | 0.2695 | 0.2695 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3104.84 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 789.8 | 0.0508 | 0.0508 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1005.46 | 0.028 | 0.028 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3637.27 | 0.23393 | 0.23393 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2324.94 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1166.78 | 0.075 | 0.075 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1596.84 | 0.0445 | 0.0445 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3915.88 | 0.25185 | 0.25185 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3100.71 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1131.13 | 0.0727 | 0.0727 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1584.05 | 0.0441 | 0.0441 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 6880.25 | 0.44251 | 0.44251 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3105.58 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 781.41 | 0.0503 | 0.0503 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1010.14 | 0.0282 | 0.0282 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6454.17 | 0.41511 | 0.41511 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2325.61 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1157.86 | 0.0745 | 0.0745 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1601.53 | 0.0446 | 0.0446 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 6892.49 | 0.4433 | 0.4433 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3099.32 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1130.97 | 0.0727 | 0.0727 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1584.05 | 0.0441 | 0.0441 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6745.51 | 0.43384 | 0.43384 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3105.52 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 781.08 | 0.0502 | 0.0502 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1010.14 | 0.0282 | 0.0282 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2899.41 | 0.18648 | 0.18648 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2325.64 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1162.77 | 0.0748 | 0.0748 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1601.53 | 0.0446 | 0.0446 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5048.39 | 0.32469 | 0.32469 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3099.49 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1166.08 | 0.075 | 0.075 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1596.84 | 0.0445 | 0.0445 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5082.25 | 0.32687 | 0.32687 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3100.55 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 784.14 | 0.0504 | 0.0504 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1005.46 | 0.028 | 0.028 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2909.63 | 0.18714 | 0.18714 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2324.94 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1134.25 | 0.073 | 0.073 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1579.42 | 0.044 | 0.044 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6771.29 | 0.4355 | 0.4355 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3104.9 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 854.64 | 0.0521 | 0.0521 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1838.53 | 0.0517 | 0.0517 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3928.28 | 0.23023 | 0.23023 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3584.36 | 0.1007 | 0.1007 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 793.25 | 0.0484 | 0.0484 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1256.85 | 0.0353 | 0.0353 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3503.71 | 0.21311 | 0.21311 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2811.52 | 0.079 | 0.079 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 919.84 | 0.0533 | 0.0533 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1858.87 | 0.0522 | 0.0522 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3868.28 | 0.22527 | 0.22527 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3577.52 | 0.10051 | 0.10051 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 849.68 | 0.0518 | 0.0518 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1828.63 | 0.0514 | 0.0514 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7274.8 | 0.43506 | 0.43506 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3575.13 | 0.10044 | 0.10044 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 787.03 | 0.048 | 0.048 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1246.84 | 0.035 | 0.035 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6918.14 | 0.4147 | 0.4147 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2801.94 | 0.0787 | 0.0787 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 910.01 | 0.0528 | 0.0528 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1848.4 | 0.0519 | 0.0519 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7281.97 | 0.4357 | 0.4357 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3565.72 | 0.10017 | 0.10017 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 849.24 | 0.0518 | 0.0518 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1829.7 | 0.0514 | 0.0514 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7073.66 | 0.42435 | 0.42435 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3576.27 | 0.10047 | 0.10047 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 786.32 | 0.0479 | 0.0479 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1256.84 | 0.0353 | 0.0353 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3283.54 | 0.19721 | 0.19721 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2811.48 | 0.079 | 0.079 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 921.44 | 0.0534 | 0.0534 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1869.33 | 0.0525 | 0.0525 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4920.36 | 0.29956 | 0.29956 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3583.3 | 0.10067 | 0.10067 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 918.97 | 0.0532 | 0.0532 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1858.88 | 0.0522 | 0.0522 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4982.93 | 0.30388 | 0.30388 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3575.99 | 0.10046 | 0.10046 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 785.21 | 0.0479 | 0.0479 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1246.84 | 0.035 | 0.035 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3294.38 | 0.19787 | 0.19787 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2802.02 | 0.0787 | 0.0787 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 848.17 | 0.0517 | 0.0517 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1819.8 | 0.0511 | 0.0511 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7106.84 | 0.42739 | 0.42739 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3567.04 | 0.10021 | 0.10021 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1361.99 | 0.0768 | 0.0768 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1658.92 | 0.0458 | 0.0458 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4861.67 | 0.27861 | 0.27861 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3325.81 | 0.0917 | 0.0917 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1091.07 | 0.0664 | 0.0664 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 960.95 | 0.0265 | 0.0265 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4101.98 | 0.24115 | 0.24115 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2444.9 | 0.0674 | 0.0674 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1462.88 | 0.0841 | 0.0841 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1679.26 | 0.0463 | 0.0463 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4926.55 | 0.28198 | 0.28198 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3310.11 | 0.0913 | 0.0913 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1354.51 | 0.0766 | 0.0766 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1647.36 | 0.0454 | 0.0454 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 8649.25 | 0.51748 | 0.51748 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3314.64 | 0.0914 | 0.0914 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1085.98 | 0.0662 | 0.0662 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 949.47 | 0.0262 | 0.0262 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8069.44 | 0.48503 | 0.48503 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2433.32 | 0.0671 | 0.0671 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1456.28 | 0.0837 | 0.0837 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1667.64 | 0.046 | 0.046 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 8659.78 | 0.52043 | 0.52043 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3296.29 | 0.0909 | 0.0909 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1353.19 | 0.0764 | 0.0764 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1648.46 | 0.0455 | 0.0455 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 8444.71 | 0.5044 | 0.5044 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3315.95 | 0.0915 | 0.0915 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1084.41 | 0.0661 | 0.0661 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 960.95 | 0.0265 | 0.0265 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4017.14 | 0.23616 | 0.23616 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2444.85 | 0.0674 | 0.0674 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1462.46 | 0.0841 | 0.0841 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1689.94 | 0.0466 | 0.0466 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5561.88 | 0.33402 | 0.33402 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3317.58 | 0.0915 | 0.0915 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1461.91 | 0.084 | 0.084 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1678.36 | 0.0463 | 0.0463 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5615.93 | 0.33733 | 0.33733 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3308.35 | 0.0913 | 0.0913 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1084.3 | 0.0661 | 0.0661 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 949.47 | 0.0262 | 0.0262 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4018.65 | 0.24142 | 0.24142 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2433.4 | 0.0671 | 0.0671 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1352.18 | 0.0764 | 0.0764 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1636.91 | 0.0452 | 0.0452 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 8467.53 | 0.50947 | 0.50947 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3304.77 | 0.0912 | 0.0912 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1501.7 | 0.0844 | 0.0844 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1794.2 | 0.0527 | 0.0527 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5608.08 | 0.32143 | 0.32143 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3442.09 | 0.10107 | 0.10107 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1144.97 | 0.0674 | 0.0674 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1064.86 | 0.0313 | 0.0313 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4749.6 | 0.27826 | 0.27826 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2551.98 | 0.0749 | 0.0749 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1574.08 | 0.0892 | 0.0892 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1829.27 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5659.97 | 0.32445 | 0.32445 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3436.6 | 0.1009 | 0.1009 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1497.33 | 0.0842 | 0.0842 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9578.91 | 0.56467 | 0.56467 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3436.88 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1139.28 | 0.0671 | 0.0671 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8930.06 | 0.52642 | 0.52642 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2546.55 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1569.16 | 0.0889 | 0.0889 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1825.32 | 0.0536 | 0.0536 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9582.38 | 0.56488 | 0.56488 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3428.53 | 0.10067 | 0.10067 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1495.44 | 0.084 | 0.084 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9460.95 | 0.55755 | 0.55755 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3436.8 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1138.34 | 0.067 | 0.067 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4668.74 | 0.27439 | 0.27439 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2546.56 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1572.58 | 0.0891 | 0.0891 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1829 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6606.44 | 0.38921 | 0.38921 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3433.16 | 0.1008 | 0.1008 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1572.73 | 0.0891 | 0.0891 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1829.02 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6671.38 | 0.39304 | 0.39304 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3435.54 | 0.10087 | 0.10087 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1138.47 | 0.0671 | 0.0671 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4670.2 | 0.27448 | 0.27448 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2546.61 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1495.49 | 0.0841 | 0.0841 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9481.42 | 0.55876 | 0.55876 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3436.83 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ10 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1935.26 | 0.10801 | 0.10801 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1835.28 | 0.0521 | 0.0521 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5422.33 | 0.3026 | 0.3026 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3791.73 | 0.10757 | 0.10757 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1342.55 | 0.0749 | 0.0749 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1007.79 | 0.0286 | 0.0286 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4220.51 | 0.23554 | 0.23554 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2773.66 | 0.0787 | 0.0787 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1970.15 | 0.10997 | 0.10997 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1879.67 | 0.0533 | 0.0533 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5431.58 | 0.30312 | 0.30312 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3796.69 | 0.10771 | 0.10771 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1926.57 | 0.10753 | 0.10753 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1848.49 | 0.0524 | 0.0524 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 8681.24 | 0.49635 | 0.49635 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3805.04 | 0.10795 | 0.10795 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1333.47 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1020.89 | 0.029 | 0.029 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 7940.66 | 0.45502 | 0.45502 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2787.13 | 0.0791 | 0.0791 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1961.52 | 0.10949 | 0.10949 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1892.89 | 0.0537 | 0.0537 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 8707.38 | 0.49805 | 0.49805 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3807.57 | 0.10802 | 0.10802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1924.92 | 0.10743 | 0.10743 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1847.15 | 0.0524 | 0.0524 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 8512.05 | 0.48375 | 0.48375 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3803.3 | 0.1079 | 0.1079 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1331.99 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1007.79 | 0.0286 | 0.0286 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4013.15 | 0.22397 | 0.22397 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2773.64 | 0.0787 | 0.0787 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1965.5 | 0.10971 | 0.10971 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1867.52 | 0.053 | 0.053 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5368.62 | 0.2996 | 0.2996 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3782.98 | 0.10732 | 0.10732 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1965.72 | 0.10972 | 0.10972 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1880.76 | 0.0534 | 0.0534 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5374.67 | 0.29994 | 0.29994 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3798.48 | 0.10776 | 0.10776 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1332.25 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1020.9 | 0.029 | 0.029 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4026.23 | 0.22978 | 0.22978 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2787.22 | 0.0791 | 0.0791 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1925.11 | 0.10744 | 0.10744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1860.37 | 0.0528 | 0.0528 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 8542.23 | 0.48547 | 0.48547 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3816.61 | 0.10828 | 0.10828 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 2324.58 | 0.13338 | 0.13338 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 774.34 | 0.0212 | 0.0212 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 6458.99 | 0.37501 | 0.37501 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4534.77 | 0.12394 | 0.12394 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1692.96 | 0.1013 | 0.1013 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 5284.41 | 0.31923 | 0.31923 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3310.7 | 0.0904 | 0.0904 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 2389.62 | 0.14133 | 0.14133 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 996.68 | 0.0273 | 0.0273 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 6533.13 | 0.38589 | 0.38589 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4538.03 | 0.12401 | 0.12401 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 2315.78 | 0.13287 | 0.13287 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 771.13 | 0.0211 | 0.0211 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9763.15 | 0.60132 | 0.60132 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4536.25 | 0.12398 | 0.12398 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1684.18 | 0.10222 | 0.10222 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8754.4 | 0.5392 | 0.5392 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3311.97 | 0.0905 | 0.0905 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 2382.24 | 0.14089 | 0.14089 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 994.16 | 0.0272 | 0.0272 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9779.78 | 0.60234 | 0.60234 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4537.35 | 0.12399 | 0.12399 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 2317.85 | 0.13299 | 0.13299 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 770.22 | 0.0211 | 0.0211 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9534.99 | 0.58616 | 0.58616 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4536.2 | 0.12398 | 0.12398 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1686.53 | 0.10092 | 0.10092 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 5218.75 | 0.31756 | 0.31756 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3310.67 | 0.0904 | 0.0904 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 2388.15 | 0.14123 | 0.14123 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1000.82 | 0.0274 | 0.0274 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6528.1 | 0.40101 | 0.40101 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4534.58 | 0.12391 | 0.12391 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 2385.93 | 0.1411 | 0.1411 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 998.31 | 0.0273 | 0.0273 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6708.14 | 0.41212 | 0.41212 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4537.89 | 0.124 | 0.124 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1684.36 | 0.10079 | 0.10079 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 5217.1 | 0.31746 | 0.31746 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3312.04 | 0.0905 | 0.0905 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 2315.74 | 0.13287 | 0.13287 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 767.01 | 0.021 | 0.021 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9571.33 | 0.58785 | 0.58785 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4537.69 | 0.12402 | 0.12402 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1217.43 | 0.0638 | 0.0638 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2133.43 | 0.0566 | 0.0566 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4738.9 | 0.2484 | 0.2484 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4380.11 | 0.11835 | 0.11835 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 919.45 | 0.0482 | 0.0482 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1155.63 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3694.95 | 0.19368 | 0.19368 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3442.08 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1273.03 | 0.0667 | 0.0667 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2238.21 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4770.61 | 0.25006 | 0.25006 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4618.07 | 0.12484 | 0.12484 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1203.14 | 0.0631 | 0.0631 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2147.85 | 0.057 | 0.057 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7633.78 | 0.40013 | 0.40013 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4391.06 | 0.11865 | 0.11865 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 905.96 | 0.0475 | 0.0475 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1167.49 | 0.0315 | 0.0315 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 7029.78 | 0.36847 | 0.36847 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3453.68 | 0.0933 | 0.0933 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1258.87 | 0.066 | 0.066 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2251.31 | 0.0604 | 0.0604 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7704.02 | 0.40382 | 0.40382 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4628.59 | 0.12512 | 0.12512 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1201.58 | 0.063 | 0.063 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2145.41 | 0.0569 | 0.0569 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7456.78 | 0.39086 | 0.39086 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4388.86 | 0.11859 | 0.11859 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 902.55 | 0.0473 | 0.0473 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1155.6 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3523.12 | 0.18467 | 0.18467 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3441.96 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1266.43 | 0.0664 | 0.0664 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2238.14 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4720.68 | 0.24744 | 0.24744 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4615.52 | 0.12477 | 0.12477 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1268.87 | 0.0665 | 0.0665 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2238.16 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4736.3 | 0.24826 | 0.24826 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4617.78 | 0.12483 | 0.12483 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 905.3 | 0.0475 | 0.0475 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1155.6 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3538.11 | 0.18546 | 0.18546 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3442 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1204.21 | 0.0631 | 0.0631 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2145.4 | 0.0569 | 0.0569 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7573.43 | 0.39697 | 0.39697 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4388.81 | 0.11859 | 0.11859 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ13 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 3160 | 0.1946 | 0.1946 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2821.51 | 0.0786 | 0.0786 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 7493.53 | 0.46111 | 0.46111 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5210.03 | 0.14519 | 0.14519 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 2414.86 | 0.1488 | 0.1488 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1827.55 | 0.0509 | 0.0509 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 6178.75 | 0.38021 | 0.38021 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3913.36 | 0.10906 | 0.10906 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 3187.49 | 0.1963 | 0.1963 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2858.02 | 0.0796 | 0.0796 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 7505.47 | 0.46184 | 0.46184 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5159.42 | 0.14378 | 0.14378 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 3157.76 | 0.19446 | 0.19446 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2838.07 | 0.0791 | 0.0791 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 10452.21 | 0.64375 | 0.64375 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5226.79 | 0.14566 | 0.14566 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 2411.49 | 0.14859 | 0.14859 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1843.99 | 0.0514 | 0.0514 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 9327.16 | 0.5753 | 0.5753 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3930.64 | 0.10954 | 0.10954 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 3186.43 | 0.19623 | 0.19623 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2874.7 | 0.0801 | 0.0801 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 10439.15 | 0.64389 | 0.64389 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5173.82 | 0.14418 | 0.14418 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 3157.16 | 0.19443 | 0.19443 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2838.08 | 0.0791 | 0.0791 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 10594.47 | 0.6531 | 0.6531 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5226.72 | 0.14565 | 0.14565 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 2407.3 | 0.14833 | 0.14833 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1843.99 | 0.0514 | 0.0514 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 6099.82 | 0.37536 | 0.37536 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3930.68 | 0.10954 | 0.10954 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 3181.79 | 0.19595 | 0.19595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2874.7 | 0.0801 | 0.0801 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 7474.48 | 0.45993 | 0.45993 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5174.03 | 0.14419 | 0.14419 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 3186.62 | 0.19624 | 0.19624 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2858.02 | 0.0796 | 0.0796 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 7486.93 | 0.4607 | 0.4607 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5159.23 | 0.14377 | 0.14377 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 2411.21 | 0.14857 | 0.14857 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1827.55 | 0.0509 | 0.0509 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 6108.87 | 0.37591 | 0.37591 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3913.37 | 0.10906 | 0.10906 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 3160.93 | 0.19466 | 0.19466 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2821.51 | 0.0786 | 0.0786 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 10691.91 | 0.65911 | 0.65911 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5210.08 | 0.14519 | 0.14519 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ14 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 2550.11 | 0.13839 | 0.13839 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1255.15 | 0.0371 | 0.0371 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 6043.55 | 0.32798 | 0.32798 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4640.41 | 0.1371 | 0.1371 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1660.91 | 0.0901 | 0.0901 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4531.32 | 0.24592 | 0.24592 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3248.15 | 0.096 | 0.096 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 2597.63 | 0.14097 | 0.14097 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1230.55 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 6074.5 | 0.32966 | 0.32966 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4621.83 | 0.13655 | 0.13655 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 2549.93 | 0.13838 | 0.13838 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1252.94 | 0.037 | 0.037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9161.94 | 0.49722 | 0.49722 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4646.24 | 0.13727 | 0.13727 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1661.63 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8143.58 | 0.44195 | 0.44195 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3253.72 | 0.0961 | 0.0961 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 2597.98 | 0.14099 | 0.14099 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1228.86 | 0.0363 | 0.0363 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9256.32 | 0.50234 | 0.50234 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4625.37 | 0.13666 | 0.13666 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 2549.11 | 0.13834 | 0.13834 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1252.33 | 0.037 | 0.037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9098.54 | 0.49378 | 0.49378 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4645.81 | 0.13726 | 0.13726 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1655.22 | 0.0898 | 0.0898 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4459.04 | 0.24199 | 0.24199 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3248.13 | 0.096 | 0.096 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 2591.4 | 0.14064 | 0.14064 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1233.36 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6255.41 | 0.33948 | 0.33948 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4614.54 | 0.13634 | 0.13634 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 2597.15 | 0.14095 | 0.14095 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1231.68 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6394.27 | 0.34702 | 0.34702 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4621.95 | 0.13655 | 0.13655 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1661.22 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4472.48 | 0.24272 | 0.24272 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3253.79 | 0.0961 | 0.0961 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 2554.89 | 0.13865 | 0.13865 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1250.13 | 0.0369 | 0.0369 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9225.36 | 0.50066 | 0.50066 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4651.63 | 0.13743 | 0.13743 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ15 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 3231.07 | 0.18011 | 0.18011 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2112.65 | 0.0592 | 0.0592 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 7725.48 | 0.43652 | 0.43652 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3985.59 | 0.11169 | 0.11169 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 2294.73 | 0.13738 | 0.13738 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1249.24 | 0.035 | 0.035 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 6237.95 | 0.36318 | 0.36318 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2899.51 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 3315.63 | 0.18912 | 0.18912 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2155.46 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 7793.71 | 0.44419 | 0.44419 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3970.98 | 0.11128 | 0.11128 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 3227.41 | 0.1799 | 0.1799 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2108.09 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 11297.85 | 0.6793 | 0.6793 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3987.23 | 0.11174 | 0.11174 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 2291.52 | 0.13719 | 0.13719 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 10045.94 | 0.60553 | 0.60553 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2901.01 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 3311.78 | 0.1889 | 0.1889 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2150.9 | 0.0603 | 0.0603 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 11412.33 | 0.69066 | 0.69066 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3970.47 | 0.11127 | 0.11127 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 3225.6 | 0.17981 | 0.17981 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2108.08 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 11086.8 | 0.66389 | 0.66389 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3987.19 | 0.11173 | 0.11173 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 2291.28 | 0.13717 | 0.13717 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 6190.58 | 0.36283 | 0.36283 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2901.05 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 3315.32 | 0.18909 | 0.18909 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2154.9 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 7936.76 | 0.47468 | 0.47468 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3969.12 | 0.11123 | 0.11123 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 3315.67 | 0.18911 | 0.18911 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2154.92 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 8121.34 | 0.49396 | 0.49396 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3970.87 | 0.11128 | 0.11128 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 2291.57 | 0.13719 | 0.13719 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 6243.57 | 0.37944 | 0.37944 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2901.08 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 3225.81 | 0.17982 | 0.17982 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2108.08 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 11245.78 | 0.68125 | 0.68125 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3987.24 | 0.11174 | 0.11174 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ16 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1814.63 | 0.11967 | 0.11967 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3072.15 | 0.0901 | 0.0901 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5812.15 | 0.38797 | 0.38797 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5533.51 | 0.16236 | 0.16236 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1290.73 | 0.0877 | 0.0877 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4750.24 | 0.32459 | 0.32459 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 4000.07 | 0.11737 | 0.11737 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1866.13 | 0.12362 | 0.12362 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3094.06 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5870.5 | 0.39393 | 0.39393 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5528.31 | 0.16221 | 0.16221 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1799.01 | 0.11864 | 0.11864 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3072.15 | 0.0901 | 0.0901 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9533.45 | 0.67542 | 0.67542 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5533.56 | 0.16236 | 0.16236 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1275.64 | 0.0869 | 0.0869 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8739.6 | 0.61918 | 0.61918 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 4000.01 | 0.11736 | 0.11736 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1851.97 | 0.12288 | 0.12288 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3094.05 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9619.84 | 0.68153 | 0.68153 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5526.26 | 0.16215 | 0.16215 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1797.79 | 0.11856 | 0.11856 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3072.96 | 0.0902 | 0.0902 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9295.91 | 0.65636 | 0.65636 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5533.15 | 0.16235 | 0.16235 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1274.25 | 0.0868 | 0.0868 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1691.34 | 0.0496 | 0.0496 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4589.08 | 0.31733 | 0.31733 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3995.49 | 0.11723 | 0.11723 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1862.69 | 0.12358 | 0.12358 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3099.4 | 0.0909 | 0.0909 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5810.41 | 0.39288 | 0.39288 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5521.88 | 0.16202 | 0.16202 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1861.04 | 0.12326 | 0.12326 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3094.07 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5822.54 | 0.39768 | 0.39768 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5528.14 | 0.1622 | 0.1622 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1272.88 | 0.0867 | 0.0867 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4608.96 | 0.32184 | 0.32184 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 4000.07 | 0.11737 | 0.11737 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1796.51 | 0.11847 | 0.11847 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3067.6 | 0.09 | 0.09 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9416.37 | 0.66711 | 0.66711 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5537.74 | 0.16248 | 0.16248 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 405.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 1484.5 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 50.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 1375.9 | 2.48 | 8.45 | 9.5 | 8.99 | 8.9
CZ01 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 333.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 1210.7 | 2.48 | 8.47 | 9.52 | 9.01 | 8.92
CZ01 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 409.6 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 4317.2 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 52.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 4302.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 335.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 4308 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 409 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 4340.5 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 50.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 831.5 | 2.5 | 8.52 | 9.58 | 9.07 | 9
CZ01 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 329.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 2414.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 331.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 2448.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 52.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 835.3 | 2.5 | 8.52 | 9.58 | 9.07 | 9.01
CZ01 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 412.9 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ01 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 4344.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1100.5 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4395.5 | 2.55 | 8.69 | 9.78 | 9.25 | 9.28
CZ02 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 890 | 2.54 | 8.67 | 9.76 | 9.24 | 9.25
CZ02 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3758.6 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ02 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1145.2 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ02 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 4447.9 | 2.55 | 8.69 | 9.79 | 9.26 | 9.29
CZ02 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1085.5 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ02 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7100.1 | 2.53 | 8.64 | 9.73 | 9.21 | 9.21
CZ02 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 873.5 | 2.54 | 8.67 | 9.76 | 9.24 | 9.25
CZ02 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6618.3 | 2.53 | 8.64 | 9.73 | 9.2 | 9.21
CZ02 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1129.9 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ02 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7106.3 | 2.53 | 8.64 | 9.73 | 9.21 | 9.21
CZ02 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1084.3 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ02 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7110.5 | 2.53 | 8.65 | 9.74 | 9.21 | 9.21
CZ02 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 872.4 | 2.54 | 8.67 | 9.76 | 9.24 | 9.25
CZ02 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3560.1 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ02 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1137.9 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ02 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4374.8 | 2.55 | 8.7 | 9.79 | 9.26 | 9.29
CZ02 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1139.1 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ02 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4384.7 | 2.55 | 8.7 | 9.79 | 9.26 | 9.29
CZ02 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 873.4 | 2.54 | 8.67 | 9.76 | 9.24 | 9.25
CZ02 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3566.2 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ02 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1085 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ02 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7128 | 2.53 | 8.65 | 9.74 | 9.21 | 9.21
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1080.9 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4231.6 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 767 | 2.5 | 8.53 | 9.59 | 9.07 | 9.01
CZ03 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3629.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1095.6 | 2.49 | 8.48 | 9.54 | 9.02 | 8.94
CZ03 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3908.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1068.9 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ03 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7195 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 755.3 | 2.5 | 8.53 | 9.59 | 9.07 | 9.02
CZ03 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6767 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1083.4 | 2.49 | 8.48 | 9.54 | 9.02 | 8.94
CZ03 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7198.5 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1069.3 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ03 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7052.4 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 759 | 2.5 | 8.53 | 9.59 | 9.07 | 9.01
CZ03 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 2883.9 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1097.3 | 2.49 | 8.48 | 9.54 | 9.02 | 8.94
CZ03 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5147.6 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1092.9 | 2.49 | 8.48 | 9.54 | 9.02 | 8.94
CZ03 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5143.2 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 755 | 2.5 | 8.53 | 9.59 | 9.07 | 9.02
CZ03 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 2875.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ03 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1065.1 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ03 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7060.5 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1234.1 | 2.56 | 8.72 | 9.83 | 9.3 | 9.34
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4597.3 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ04 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 997.1 | 2.55 | 8.69 | 9.79 | 9.26 | 9.28
CZ04 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3919.2 | 2.54 | 8.68 | 9.77 | 9.24 | 9.26
CZ04 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1276.7 | 2.55 | 8.72 | 9.82 | 9.29 | 9.33
CZ04 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 4638.8 | 2.55 | 8.7 | 9.8 | 9.27 | 9.31
CZ04 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1222.9 | 2.56 | 8.72 | 9.83 | 9.3 | 9.34
CZ04 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7306.8 | 2.54 | 8.66 | 9.75 | 9.22 | 9.23
CZ04 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 985.6 | 2.55 | 8.69 | 9.79 | 9.26 | 9.28
CZ04 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6782.7 | 2.54 | 8.65 | 9.74 | 9.22 | 9.22
CZ04 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1266.1 | 2.55 | 8.72 | 9.82 | 9.29 | 9.33
CZ04 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7306.6 | 2.54 | 8.66 | 9.75 | 9.22 | 9.23
CZ04 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1222.6 | 2.56 | 8.72 | 9.83 | 9.3 | 9.34
CZ04 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7319 | 2.54 | 8.66 | 9.75 | 9.22 | 9.23
CZ04 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 985.1 | 2.55 | 8.69 | 9.79 | 9.26 | 9.28
CZ04 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3782.1 | 2.54 | 8.68 | 9.77 | 9.24 | 9.26
CZ04 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1272.3 | 2.55 | 8.72 | 9.82 | 9.29 | 9.33
CZ04 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4601.6 | 2.55 | 8.7 | 9.8 | 9.27 | 9.31
CZ04 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1272.4 | 2.55 | 8.72 | 9.82 | 9.29 | 9.33
CZ04 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4602.8 | 2.55 | 8.7 | 9.8 | 9.27 | 9.31
CZ04 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 984.9 | 2.55 | 8.69 | 9.79 | 9.26 | 9.28
CZ04 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3782.4 | 2.54 | 8.68 | 9.77 | 9.24 | 9.26
CZ04 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1222.1 | 2.56 | 8.72 | 9.83 | 9.3 | 9.34
CZ04 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7332.9 | 2.54 | 8.66 | 9.75 | 9.22 | 9.23
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1098.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 3910.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 686.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3195.2 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1136.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3887.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1104.4 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7346.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 691.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6981.4 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1141.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7334.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1103.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7149.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 686.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 2900.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1130.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4562.9 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1136.4 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4584.1 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 691.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 2896.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1109.4 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ05 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7171.7 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1148.7 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4138.2 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ06 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 797 | 2.49 | 8.5 | 9.55 | 9.03 | 8.96
CZ06 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3592 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ06 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1173.5 | 2.49 | 8.49 | 9.54 | 9.03 | 8.95
CZ06 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3867.2 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ06 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1139.8 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ06 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 6827.9 | 2.48 | 8.46 | 9.51 | 9 | 8.91
CZ06 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 788.5 | 2.49 | 8.5 | 9.55 | 9.03 | 8.96
CZ06 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6404.8 | 2.48 | 8.46 | 9.51 | 9 | 8.91
CZ06 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1164.5 | 2.49 | 8.49 | 9.54 | 9.03 | 8.95
CZ06 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 6839.6 | 2.48 | 8.46 | 9.51 | 9 | 8.91
CZ06 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1139.6 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ06 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 6701.9 | 2.48 | 8.47 | 9.52 | 9 | 8.91
CZ06 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 788.2 | 2.49 | 8.5 | 9.55 | 9.04 | 8.96
CZ06 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 2903.6 | 2.49 | 8.48 | 9.53 | 9.02 | 8.94
CZ06 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1169.5 | 2.49 | 8.49 | 9.54 | 9.03 | 8.95
CZ06 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4985.6 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ06 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1172.8 | 2.49 | 8.49 | 9.54 | 9.03 | 8.95
CZ06 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5019 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ06 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 791.3 | 2.49 | 8.5 | 9.55 | 9.03 | 8.96
CZ06 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 2913.8 | 2.49 | 8.48 | 9.53 | 9.02 | 8.94
CZ06 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1142.9 | 2.49 | 8.49 | 9.55 | 9.03 | 8.96
CZ06 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 6727.3 | 2.48 | 8.47 | 9.52 | 9 | 8.91
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 984.3 | 2.56 | 8.74 | 9.84 | 9.31 | 9.36
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 3956.8 | 2.54 | 8.66 | 9.75 | 9.23 | 9.24
CZ07 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 873.3 | 2.56 | 8.75 | 9.86 | 9.32 | 9.38
CZ07 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3558.2 | 2.52 | 8.61 | 9.69 | 9.17 | 9.15
CZ07 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1152 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ07 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3930.9 | 2.55 | 8.69 | 9.79 | 9.26 | 9.28
CZ07 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 979.3 | 2.56 | 8.74 | 9.84 | 9.31 | 9.36
CZ07 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7284 | 2.52 | 8.61 | 9.7 | 9.17 | 9.16
CZ07 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 867 | 2.56 | 8.75 | 9.86 | 9.33 | 9.38
CZ07 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6936.3 | 2.52 | 8.61 | 9.69 | 9.17 | 9.15
CZ07 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1146.3 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ07 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7291.4 | 2.52 | 8.61 | 9.69 | 9.17 | 9.16
CZ07 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 977.1 | 2.56 | 8.74 | 9.84 | 9.31 | 9.36
CZ07 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7087.4 | 2.52 | 8.61 | 9.69 | 9.17 | 9.15
CZ07 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 866.2 | 2.56 | 8.75 | 9.86 | 9.33 | 9.38
CZ07 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3368.7 | 2.54 | 8.65 | 9.74 | 9.21 | 9.22
CZ07 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1154.8 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ07 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4901.6 | 2.51 | 8.57 | 9.65 | 9.12 | 9.09
CZ07 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1151.6 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ07 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4963.5 | 2.51 | 8.57 | 9.64 | 9.12 | 9.08
CZ07 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 865.1 | 2.56 | 8.75 | 9.86 | 9.33 | 9.38
CZ07 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3379.4 | 2.54 | 8.65 | 9.74 | 9.21 | 9.22
CZ07 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 974.1 | 2.56 | 8.74 | 9.84 | 9.31 | 9.36
CZ07 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7122.9 | 2.52 | 8.61 | 9.69 | 9.16 | 9.14
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1439.9 | 2.58 | 8.81 | 9.94 | 9.4 | 9.49
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4996.3 | 2.56 | 8.74 | 9.84 | 9.31 | 9.36
CZ08 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1164.1 | 2.55 | 8.7 | 9.79 | 9.26 | 9.29
CZ08 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4226.7 | 2.55 | 8.7 | 9.8 | 9.27 | 9.29
CZ08 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1544.1 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ08 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5062 | 2.56 | 8.74 | 9.85 | 9.31 | 9.37
CZ08 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1432.4 | 2.58 | 8.81 | 9.93 | 9.39 | 9.48
CZ08 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 8817.5 | 2.53 | 8.65 | 9.73 | 9.21 | 9.21
CZ08 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1159 | 2.55 | 8.69 | 9.79 | 9.26 | 9.29
CZ08 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 8231.5 | 2.53 | 8.64 | 9.73 | 9.2 | 9.2
CZ08 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1537.4 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ08 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 8827.4 | 2.53 | 8.64 | 9.72 | 9.2 | 9.2
CZ08 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1431 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ08 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 8612.4 | 2.54 | 8.65 | 9.74 | 9.21 | 9.22
CZ08 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1157.4 | 2.55 | 8.69 | 9.79 | 9.26 | 9.29
CZ08 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4140.9 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ08 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1543.6 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ08 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5518.1 | 2.52 | 8.59 | 9.67 | 9.14 | 9.12
CZ08 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1543.1 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ08 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5569.4 | 2.52 | 8.59 | 9.67 | 9.14 | 9.12
CZ08 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1157.3 | 2.55 | 8.69 | 9.79 | 9.26 | 9.29
CZ08 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4142.5 | 2.54 | 8.66 | 9.75 | 9.22 | 9.23
CZ08 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1430 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ08 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 8632.4 | 2.53 | 8.64 | 9.72 | 9.2 | 9.19
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1529.3 | 2.57 | 8.75 | 9.87 | 9.33 | 9.39
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5713.3 | 2.56 | 8.72 | 9.82 | 9.29 | 9.34
CZ09 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1166.1 | 2.54 | 8.67 | 9.77 | 9.24 | 9.25
CZ09 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4836.9 | 2.54 | 8.68 | 9.78 | 9.25 | 9.27
CZ09 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1603 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ09 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5763.9 | 2.56 | 8.72 | 9.82 | 9.29 | 9.33
CZ09 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1524.9 | 2.57 | 8.75 | 9.87 | 9.33 | 9.39
CZ09 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9729.2 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ09 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1160.3 | 2.54 | 8.67 | 9.77 | 9.24 | 9.25
CZ09 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9066.8 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ09 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1598 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ09 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9732 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ09 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1523 | 2.57 | 8.75 | 9.87 | 9.33 | 9.39
CZ09 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9612.4 | 2.54 | 8.67 | 9.76 | 9.23 | 9.25
CZ09 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1159.3 | 2.54 | 8.67 | 9.77 | 9.24 | 9.25
CZ09 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4754.2 | 2.54 | 8.68 | 9.77 | 9.24 | 9.26
CZ09 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1601.5 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ09 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6508.9 | 2.52 | 8.61 | 9.69 | 9.17 | 9.15
CZ09 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1601.7 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ09 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6571.5 | 2.52 | 8.61 | 9.69 | 9.17 | 9.15
CZ09 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1159.5 | 2.54 | 8.67 | 9.77 | 9.24 | 9.25
CZ09 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4755.7 | 2.54 | 8.68 | 9.77 | 9.24 | 9.26
CZ09 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1523 | 2.57 | 8.75 | 9.87 | 9.33 | 9.39
CZ09 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9627.7 | 2.54 | 8.67 | 9.76 | 9.23 | 9.24
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2173.6 | 2.62 | 8.93 | 10.08 | 9.53 | 9.69
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5910.3 | 2.6 | 8.88 | 10.02 | 9.48 | 9.61
CZ10 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1535.3 | 2.63 | 8.96 | 10.11 | 9.57 | 9.74
CZ10 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4624 | 2.61 | 8.89 | 10.03 | 9.49 | 9.62
CZ10 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2208.8 | 2.62 | 8.93 | 10.07 | 9.53 | 9.69
CZ10 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5919.8 | 2.6 | 8.88 | 10.02 | 9.48 | 9.61
CZ10 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2164.5 | 2.62 | 8.93 | 10.08 | 9.53 | 9.7
CZ10 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9125.4 | 2.57 | 8.78 | 9.9 | 9.36 | 9.44
CZ10 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1525.9 | 2.63 | 8.96 | 10.11 | 9.57 | 9.75
CZ10 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 8352.6 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ10 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2199.7 | 2.62 | 8.93 | 10.08 | 9.53 | 9.69
CZ10 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9151.4 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ10 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2162.8 | 2.62 | 8.93 | 10.08 | 9.53 | 9.7
CZ10 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9002.9 | 2.58 | 8.8 | 9.92 | 9.38 | 9.47
CZ10 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1524.3 | 2.63 | 8.96 | 10.11 | 9.57 | 9.75
CZ10 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4404 | 2.61 | 8.89 | 10.03 | 9.49 | 9.63
CZ10 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2203.9 | 2.62 | 8.93 | 10.08 | 9.53 | 9.69
CZ10 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5853.2 | 2.6 | 8.88 | 10.02 | 9.48 | 9.61
CZ10 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2204.1 | 2.62 | 8.93 | 10.08 | 9.53 | 9.69
CZ10 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5859.6 | 2.6 | 8.88 | 10.02 | 9.48 | 9.61
CZ10 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1524.5 | 2.63 | 8.96 | 10.11 | 9.57 | 9.75
CZ10 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4336.3 | 2.59 | 8.82 | 9.95 | 9.41 | 9.51
CZ10 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2163 | 2.62 | 8.93 | 10.08 | 9.53 | 9.7
CZ10 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9033.9 | 2.58 | 8.8 | 9.92 | 9.38 | 9.47
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2539.4 | 2.59 | 8.84 | 9.97 | 9.43 | 9.54
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 7030.4 | 2.58 | 8.81 | 9.94 | 9.4 | 9.49
CZ11 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1827.4 | 2.56 | 8.75 | 9.86 | 9.32 | 9.38
CZ11 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5689.7 | 2.56 | 8.73 | 9.83 | 9.3 | 9.34
CZ11 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2587.1 | 2.57 | 8.77 | 9.89 | 9.35 | 9.42
CZ11 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 7073.7 | 2.57 | 8.77 | 9.89 | 9.35 | 9.43
CZ11 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2529.8 | 2.59 | 8.84 | 9.97 | 9.43 | 9.54
CZ11 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10448.6 | 2.54 | 8.68 | 9.78 | 9.25 | 9.27
CZ11 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1811.9 | 2.55 | 8.72 | 9.82 | 9.29 | 9.33
CZ11 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9369.2 | 2.54 | 8.68 | 9.78 | 9.25 | 9.27
CZ11 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2579.1 | 2.57 | 8.77 | 9.89 | 9.35 | 9.42
CZ11 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10466.4 | 2.54 | 8.68 | 9.78 | 9.25 | 9.27
CZ11 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2532.1 | 2.59 | 8.84 | 9.97 | 9.43 | 9.54
CZ11 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10210.1 | 2.55 | 8.69 | 9.78 | 9.25 | 9.28
CZ11 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1820.4 | 2.56 | 8.75 | 9.86 | 9.32 | 9.38
CZ11 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5606.5 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ11 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2585.5 | 2.57 | 8.77 | 9.89 | 9.35 | 9.42
CZ11 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6612.2 | 2.52 | 8.59 | 9.66 | 9.14 | 9.11
CZ11 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2583.1 | 2.57 | 8.77 | 9.89 | 9.35 | 9.42
CZ11 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6785.2 | 2.52 | 8.58 | 9.66 | 9.14 | 9.11
CZ11 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1818.1 | 2.56 | 8.75 | 9.86 | 9.32 | 9.38
CZ11 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5604.7 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ11 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2529.8 | 2.59 | 8.84 | 9.97 | 9.43 | 9.54
CZ11 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10251.8 | 2.55 | 8.69 | 9.78 | 9.26 | 9.28
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1373.3 | 2.65 | 9.04 | 10.21 | 9.66 | 9.88
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5107.7 | 2.63 | 8.96 | 10.12 | 9.57 | 9.76
CZ12 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1045.3 | 2.65 | 9.05 | 10.22 | 9.67 | 9.9
CZ12 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3975.2 | 2.63 | 8.96 | 10.12 | 9.57 | 9.75
CZ12 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1544.8 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ12 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5127.2 | 2.63 | 8.96 | 10.12 | 9.57 | 9.75
CZ12 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1356.4 | 2.65 | 9.03 | 10.21 | 9.66 | 9.88
CZ12 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7804.6 | 2.6 | 8.88 | 10.02 | 9.48 | 9.61
CZ12 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1030.8 | 2.65 | 9.05 | 10.22 | 9.67 | 9.91
CZ12 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 7169.9 | 2.6 | 8.87 | 10.01 | 9.47 | 9.6
CZ12 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1541.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ12 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7837.5 | 2.6 | 8.87 | 10.01 | 9.47 | 9.59
CZ12 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1354.7 | 2.65 | 9.03 | 10.21 | 9.66 | 9.88
CZ12 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7656.9 | 2.6 | 8.89 | 10.03 | 9.48 | 9.62
CZ12 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1027 | 2.65 | 9.05 | 10.22 | 9.67 | 9.91
CZ12 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3765.5 | 2.62 | 8.95 | 10.1 | 9.56 | 9.73
CZ12 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1537.8 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ12 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5070.9 | 2.63 | 8.96 | 10.11 | 9.57 | 9.75
CZ12 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1538.9 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ12 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5087.4 | 2.63 | 8.96 | 10.11 | 9.57 | 9.75
CZ12 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1030.1 | 2.65 | 9.05 | 10.22 | 9.67 | 9.91
CZ12 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3787.2 | 2.62 | 8.95 | 10.11 | 9.56 | 9.74
CZ12 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1357.5 | 2.65 | 9.03 | 10.21 | 9.66 | 9.88
CZ12 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7756.6 | 2.6 | 8.88 | 10.02 | 9.48 | 9.61
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 3569.8 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 8260.5 | 2.56 | 8.73 | 9.84 | 9.31 | 9.36
CZ13 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2758.9 | 2.58 | 8.79 | 9.91 | 9.38 | 9.46
CZ13 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 6840.3 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ13 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3597.2 | 2.57 | 8.77 | 9.89 | 9.35 | 9.43
CZ13 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 8272.6 | 2.56 | 8.73 | 9.84 | 9.31 | 9.36
CZ13 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 3567.4 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ13 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 11373.6 | 2.55 | 8.71 | 9.81 | 9.28 | 9.32
CZ13 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2755.2 | 2.58 | 8.79 | 9.91 | 9.38 | 9.46
CZ13 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 10074.5 | 2.55 | 8.69 | 9.79 | 9.26 | 9.29
CZ13 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3596 | 2.57 | 8.77 | 9.89 | 9.35 | 9.43
CZ13 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 11272.8 | 2.55 | 8.69 | 9.79 | 9.26 | 9.29
CZ13 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 3566.7 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ13 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 11465.9 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ13 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2750.6 | 2.58 | 8.79 | 9.91 | 9.38 | 9.46
CZ13 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 6755 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ13 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3591 | 2.57 | 8.77 | 9.89 | 9.35 | 9.43
CZ13 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 8239.1 | 2.56 | 8.73 | 9.84 | 9.31 | 9.36
CZ13 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3596.3 | 2.57 | 8.77 | 9.89 | 9.35 | 9.43
CZ13 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 8252.5 | 2.56 | 8.73 | 9.84 | 9.31 | 9.36
CZ13 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2754.9 | 2.58 | 8.79 | 9.91 | 9.38 | 9.46
CZ13 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 6764.8 | 2.56 | 8.74 | 9.85 | 9.32 | 9.37
CZ13 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3570.8 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ13 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 11568.4 | 2.55 | 8.7 | 9.8 | 9.27 | 9.3
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2859.9 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6761.1 | 2.63 | 8.97 | 10.13 | 9.58 | 9.76
CZ14 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1863.1 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5051.5 | 2.63 | 8.96 | 10.12 | 9.57 | 9.75
CZ14 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2913.2 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6790.1 | 2.63 | 8.97 | 10.12 | 9.58 | 9.76
CZ14 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2859.7 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9873.2 | 2.61 | 8.91 | 10.05 | 9.51 | 9.66
CZ14 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1863.9 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 8757.3 | 2.61 | 8.9 | 10.05 | 9.5 | 9.65
CZ14 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2913.6 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9945.2 | 2.61 | 8.9 | 10.05 | 9.5 | 9.65
CZ14 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2858.8 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9867.4 | 2.61 | 8.92 | 10.06 | 9.52 | 9.67
CZ14 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1856.7 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4963.2 | 2.63 | 8.96 | 10.12 | 9.57 | 9.75
CZ14 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2906.3 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6414.1 | 2.59 | 8.83 | 9.95 | 9.41 | 9.51
CZ14 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2912.7 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6539 | 2.59 | 8.82 | 9.95 | 9.41 | 9.51
CZ14 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1863.5 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4978.1 | 2.63 | 8.96 | 10.12 | 9.57 | 9.75
CZ14 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2865.3 | 2.63 | 8.97 | 10.13 | 9.58 | 9.77
CZ14 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9990.3 | 2.61 | 8.92 | 10.06 | 9.52 | 9.67
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 3675 | 2.62 | 8.95 | 10.11 | 9.56 | 9.73
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 8773.5 | 2.62 | 8.93 | 10.08 | 9.53 | 9.69
CZ15 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2572.3 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ15 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 7041.9 | 2.6 | 8.87 | 10 | 9.46 | 9.59
CZ15 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3748.6 | 2.61 | 8.9 | 10.05 | 9.51 | 9.65
CZ15 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 8831.8 | 2.61 | 8.91 | 10.05 | 9.51 | 9.66
CZ15 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 3670.9 | 2.62 | 8.95 | 10.11 | 9.56 | 9.73
CZ15 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 12646.1 | 2.58 | 8.8 | 9.92 | 9.39 | 9.47
CZ15 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2568.7 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ15 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 11237.5 | 2.58 | 8.8 | 9.92 | 9.38 | 9.46
CZ15 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3744.3 | 2.61 | 8.9 | 10.05 | 9.51 | 9.65
CZ15 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 12752.2 | 2.58 | 8.79 | 9.9 | 9.37 | 9.45
CZ15 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 3668.8 | 2.62 | 8.95 | 10.11 | 9.56 | 9.73
CZ15 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 12423.5 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ15 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2568.4 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ15 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 6978.9 | 2.6 | 8.86 | 9.99 | 9.45 | 9.57
CZ15 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3748.3 | 2.61 | 8.9 | 10.05 | 9.51 | 9.65
CZ15 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 8424.4 | 2.56 | 8.72 | 9.82 | 9.29 | 9.33
CZ15 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3748.7 | 2.61 | 8.9 | 10.05 | 9.51 | 9.65
CZ15 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 8590.1 | 2.54 | 8.68 | 9.78 | 9.25 | 9.27
CZ15 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2568.7 | 2.58 | 8.81 | 9.93 | 9.4 | 9.49
CZ15 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 6969.3 | 2.57 | 8.78 | 9.89 | 9.36 | 9.43
CZ15 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3669 | 2.62 | 8.95 | 10.11 | 9.56 | 9.73
CZ15 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 12562.7 | 2.57 | 8.78 | 9.9 | 9.37 | 9.44
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1976.2 | 2.52 | 8.59 | 9.67 | 9.14 | 9.12
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6291 | 2.51 | 8.56 | 9.63 | 9.1 | 9.06
CZ16 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1389.8 | 2.49 | 8.51 | 9.57 | 9.06 | 8.99
CZ16 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5101.2 | 2.49 | 8.5 | 9.55 | 9.04 | 8.97
CZ16 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2025.1 | 2.51 | 8.58 | 9.65 | 9.13 | 9.09
CZ16 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6342.3 | 2.5 | 8.54 | 9.61 | 9.09 | 9.04
CZ16 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1959.2 | 2.52 | 8.59 | 9.67 | 9.14 | 9.12
CZ16 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10370.9 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ16 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1372.1 | 2.49 | 8.51 | 9.56 | 9.05 | 8.98
CZ16 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9507.5 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ16 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2008.2 | 2.51 | 8.57 | 9.64 | 9.12 | 9.09
CZ16 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10464.9 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ16 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1957.9 | 2.52 | 8.59 | 9.67 | 9.14 | 9.12
CZ16 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10078.3 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ16 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1370.6 | 2.49 | 8.51 | 9.56 | 9.05 | 8.98
CZ16 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4902.9 | 2.48 | 8.47 | 9.52 | 9 | 8.91
CZ16 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2019.9 | 2.51 | 8.57 | 9.64 | 9.12 | 9.09
CZ16 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6255.6 | 2.5 | 8.52 | 9.58 | 9.07 | 9.01
CZ16 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2019.7 | 2.51 | 8.58 | 9.65 | 9.13 | 9.09
CZ16 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6241.1 | 2.49 | 8.5 | 9.55 | 9.04 | 8.96
CZ16 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1369.1 | 2.49 | 8.51 | 9.56 | 9.05 | 8.98
CZ16 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4941.8 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
CZ16 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1956.5 | 2.52 | 8.59 | 9.67 | 9.14 | 9.12
CZ16 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10243.4 | 2.48 | 8.45 | 9.5 | 8.99 | 8.89
SWHC049-03 SEER Rated AC HP_DMo | DMo&0&rDXGF&Ex&dxAC_equip | dxAC-Res-SEER-13.0
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL1 | Cooling | Sensible | 2428.32 | 0.18655 | 0.18655 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL1 | Heating | Sensible | 3751.47 | 0.0874 | 0.0874 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ01 | 3 | DXGF EL2 | Cooling | Sensible | 3044.65 | 0.23389 | 0.23389 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL2 | Heating | Sensible | 3746.03 | 0.0872 | 0.0872 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ02 | 1 | DXGF EL1 | Cooling | Sensible | 6665.45 | 0.37583 | 0.37583 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL1 | Heating | Sensible | 5400.93 | 0.13973 | 0.13973 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ02 | 3 | DXGF EL2 | Cooling | Sensible | 6809.42 | 0.38442 | 0.38442 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL2 | Heating | Sensible | 5385.24 | 0.13933 | 0.13933 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ03 | 1 | DXGF EL1 | Cooling | Sensible | 6392.15 | 0.44562 | 0.44562 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL1 | Heating | Sensible | 4334.93 | 0.11346 | 0.11346 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ03 | 3 | DXGF EL2 | Cooling | Sensible | 6259.28 | 0.43636 | 0.43636 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL2 | Heating | Sensible | 4329.87 | 0.11333 | 0.11333 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 1 | DXGF EL1 | Cooling | Sensible | 6367.64 | 0.3687 | 0.3687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL1 | Heating | Sensible | 4598.25 | 0.12019 | 0.12019 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 3 | DXGF EL2 | Cooling | Sensible | 6742.82 | 0.39556 | 0.39556 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL2 | Heating | Sensible | 4592.43 | 0.12004 | 0.12004 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ05 | 1 | DXGF EL1 | Cooling | Sensible | 6374.55 | 0.44682 | 0.44682 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL1 | Heating | Sensible | 5152.73 | 0.1356 | 0.1356 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ05 | 3 | DXGF EL2 | Cooling | Sensible | 6421.37 | 0.4501 | 0.4501 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL2 | Heating | Sensible | 5147.5 | 0.13546 | 0.13546 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ06 | 1 | DXGF EL1 | Cooling | Sensible | 5556.17 | 0.37849 | 0.37849 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL1 | Heating | Sensible | 2697.81 | 0.0677 | 0.0677 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ06 | 3 | DXGF EL2 | Cooling | Sensible | 6162.84 | 0.41953 | 0.41953 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL2 | Heating | Sensible | 2692.95 | 0.0676 | 0.0676 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 1 | DXGF EL1 | Cooling | Sensible | 6794.57 | 0.43755 | 0.43755 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL1 | Heating | Sensible | 2294.96 | 0.0551 | 0.0551 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 3 | DXGF EL2 | Cooling | Sensible | 7412.75 | 0.49074 | 0.49074 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL2 | Heating | Sensible | 2289.88 | 0.055 | 0.055 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 1 | DXGF EL1 | Cooling | Sensible | 6694.03 | 0.41268 | 0.41268 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL1 | Heating | Sensible | 2654.94 | 0.0638 | 0.0638 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 3 | DXGF EL2 | Cooling | Sensible | 7593.75 | 0.45555 | 0.45555 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL2 | Heating | Sensible | 2649.77 | 0.0637 | 0.0637 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ09 | 1 | DXGF EL1 | Cooling | Sensible | 8698.51 | 0.57024 | 0.57024 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL1 | Heating | Sensible | 5759.41 | 0.15909 | 0.15909 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL2 | Cooling | Sensible | 9537.01 | 0.59463 | 0.59463 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL2 | Heating | Sensible | 5755.75 | 0.15899 | 0.15899 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL1 | Cooling | Sensible | 7245.53 | 0.40469 | 0.40469 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL1 | Heating | Sensible | 5223.16 | 0.14818 | 0.14818 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ10 | 3 | DXGF EL2 | Cooling | Sensible | 7338.42 | 0.4104 | 0.4104 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL2 | Heating | Sensible | 5217.44 | 0.14802 | 0.14802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ11 | 1 | DXGF EL1 | Cooling | Sensible | 9489.56 | 0.55446 | 0.55446 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL1 | Heating | Sensible | 7898.8 | 0.21968 | 0.21968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL2 | Cooling | Sensible | 9947.67 | 0.61253 | 0.61253 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL2 | Heating | Sensible | 7893.59 | 0.21954 | 0.21954 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL1 | Cooling | Sensible | 8404.91 | 0.48411 | 0.48411 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL1 | Heating | Sensible | 6372.52 | 0.17567 | 0.17567 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ12 | 3 | DXGF EL2 | Cooling | Sensible | 8115.46 | 0.47569 | 0.47569 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL2 | Heating | Sensible | 6377.57 | 0.17581 | 0.17581 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ13 | 1 | DXGF EL1 | Cooling | Sensible | 8884.13 | 0.51893 | 0.51893 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL1 | Heating | Sensible | 6129.53 | 0.17081 | 0.17081 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ13 | 3 | DXGF EL2 | Cooling | Sensible | 9350.58 | 0.57174 | 0.57174 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL2 | Heating | Sensible | 6122.71 | 0.17062 | 0.17062 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 1 | DXGF EL1 | Cooling | Sensible | 8511.58 | 0.47812 | 0.47812 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL1 | Heating | Sensible | 7537.4 | 0.24293 | 0.24293 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 3 | DXGF EL2 | Cooling | Sensible | 8579.52 | 0.48194 | 0.48194 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL2 | Heating | Sensible | 7532.51 | 0.24277 | 0.24277 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ15 | 1 | DXGF EL1 | Cooling | Sensible | 10860.35 | 0.61866 | 0.61866 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL1 | Heating | Sensible | 6496.97 | 0.18523 | 0.18523 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL2 | Cooling | Sensible | 11216.29 | 0.66796 | 0.66796 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL2 | Heating | Sensible | 6494.09 | 0.18515 | 0.18515 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL1 | Cooling | Sensible | 8239.72 | 0.55403 | 0.55403 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL1 | Heating | Sensible | 6835.19 | 0.18489 | 0.18489 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL2 | Cooling | Sensible | 8991.75 | 0.63248 | 0.63248 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL2 | Heating | Sensible | 6828.3 | 0.1847 | 0.1847 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 2917.8 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 3658.3 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6810.8 | 2.71 | 9.25 | 10.47 | 9.9 | 10.26
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6871 | 2.7 | 9.23 | 10.44 | 9.88 | 10.23
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6970 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6825.1 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6540.9 | 2.7 | 9.22 | 10.43 | 9.87 | 10.21
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6887.2 | 2.69 | 9.19 | 10.4 | 9.83 | 10.16
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6988.7 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7040 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 5920 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6561.8 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 7041.9 | 2.66 | 9.07 | 10.25 | 9.7 | 9.95
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7686.1 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6951.8 | 2.68 | 9.14 | 10.34 | 9.78 | 10.07
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7865.9 | 2.69 | 9.18 | 10.38 | 9.82 | 10.14
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9085.1 | 2.65 | 9.06 | 10.23 | 9.68 | 9.92
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9922.2 | 2.67 | 9.13 | 10.32 | 9.76 | 10.05
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 7898.2 | 2.74 | 9.35 | 10.59 | 10.02 | 10.45
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7864.6 | 2.73 | 9.32 | 10.56 | 9.99 | 10.41
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10467.3 | 2.73 | 9.3 | 10.54 | 9.97 | 10.37
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10825.9 | 2.7 | 9.21 | 10.42 | 9.86 | 10.2
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9132 | 2.73 | 9.3 | 10.54 | 9.97 | 10.37
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 8635.9 | 2.71 | 9.25 | 10.47 | 9.9 | 10.27
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9830.6 | 2.73 | 9.31 | 10.54 | 9.97 | 10.38
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10233.3 | 2.7 | 9.23 | 10.45 | 9.88 | 10.23
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9617.6 | 2.75 | 9.39 | 10.64 | 10.07 | 10.53
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9452.2 | 2.74 | 9.35 | 10.6 | 10.03 | 10.47
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 12486.7 | 2.75 | 9.39 | 10.65 | 10.07 | 10.54
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 12782.7 | 2.73 | 9.32 | 10.56 | 9.99 | 10.4
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9047.1 | 2.67 | 9.09 | 10.28 | 9.73 | 9.99
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9892.7 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
SWHC049-03 SEER Rated AC HP_DMo | DMo&0&rDXHP&Ex&dxHP_equip | HSPF_7p0_SEER_13_Pre
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL1 | Cooling | Sensible | 2428.32 | 0.18655 | 0.18655 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL1 | Heating | Sensible | 3751.47 | 0.0874 | 0.0874 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ01 | 3 | DXGF EL2 | Cooling | Sensible | 3044.65 | 0.23389 | 0.23389 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL2 | Heating | Sensible | 3746.03 | 0.0872 | 0.0872 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ02 | 1 | DXGF EL1 | Cooling | Sensible | 6665.45 | 0.37583 | 0.37583 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL1 | Heating | Sensible | 5400.93 | 0.13973 | 0.13973 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ02 | 3 | DXGF EL2 | Cooling | Sensible | 6809.42 | 0.38442 | 0.38442 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL2 | Heating | Sensible | 5385.24 | 0.13933 | 0.13933 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ03 | 1 | DXGF EL1 | Cooling | Sensible | 6392.15 | 0.44562 | 0.44562 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL1 | Heating | Sensible | 4334.93 | 0.11346 | 0.11346 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ03 | 3 | DXGF EL2 | Cooling | Sensible | 6259.28 | 0.43636 | 0.43636 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL2 | Heating | Sensible | 4329.87 | 0.11333 | 0.11333 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 1 | DXGF EL1 | Cooling | Sensible | 6367.64 | 0.3687 | 0.3687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL1 | Heating | Sensible | 4598.25 | 0.12019 | 0.12019 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 3 | DXGF EL2 | Cooling | Sensible | 6742.82 | 0.39556 | 0.39556 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL2 | Heating | Sensible | 4592.43 | 0.12004 | 0.12004 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ05 | 1 | DXGF EL1 | Cooling | Sensible | 6374.55 | 0.44682 | 0.44682 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL1 | Heating | Sensible | 5152.73 | 0.1356 | 0.1356 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ05 | 3 | DXGF EL2 | Cooling | Sensible | 6421.37 | 0.4501 | 0.4501 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL2 | Heating | Sensible | 5147.5 | 0.13546 | 0.13546 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ06 | 1 | DXGF EL1 | Cooling | Sensible | 5556.17 | 0.37849 | 0.37849 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL1 | Heating | Sensible | 2697.81 | 0.0677 | 0.0677 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ06 | 3 | DXGF EL2 | Cooling | Sensible | 6162.84 | 0.41953 | 0.41953 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL2 | Heating | Sensible | 2692.95 | 0.0676 | 0.0676 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 1 | DXGF EL1 | Cooling | Sensible | 6794.57 | 0.43755 | 0.43755 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL1 | Heating | Sensible | 2294.96 | 0.0551 | 0.0551 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 3 | DXGF EL2 | Cooling | Sensible | 7412.75 | 0.49074 | 0.49074 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL2 | Heating | Sensible | 2289.88 | 0.055 | 0.055 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 1 | DXGF EL1 | Cooling | Sensible | 6694.03 | 0.41268 | 0.41268 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL1 | Heating | Sensible | 2654.94 | 0.0638 | 0.0638 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 3 | DXGF EL2 | Cooling | Sensible | 7593.75 | 0.45555 | 0.45555 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL2 | Heating | Sensible | 2649.77 | 0.0637 | 0.0637 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ09 | 1 | DXGF EL1 | Cooling | Sensible | 8698.51 | 0.57024 | 0.57024 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL1 | Heating | Sensible | 5759.41 | 0.15909 | 0.15909 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL2 | Cooling | Sensible | 9537.01 | 0.59463 | 0.59463 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL2 | Heating | Sensible | 5755.75 | 0.15899 | 0.15899 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL1 | Cooling | Sensible | 7245.53 | 0.40469 | 0.40469 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL1 | Heating | Sensible | 5223.16 | 0.14818 | 0.14818 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ10 | 3 | DXGF EL2 | Cooling | Sensible | 7338.42 | 0.4104 | 0.4104 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL2 | Heating | Sensible | 5217.44 | 0.14802 | 0.14802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ11 | 1 | DXGF EL1 | Cooling | Sensible | 9489.56 | 0.55446 | 0.55446 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL1 | Heating | Sensible | 7898.8 | 0.21968 | 0.21968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL2 | Cooling | Sensible | 9947.67 | 0.61253 | 0.61253 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL2 | Heating | Sensible | 7893.59 | 0.21954 | 0.21954 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL1 | Cooling | Sensible | 8404.91 | 0.48411 | 0.48411 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL1 | Heating | Sensible | 6372.52 | 0.17567 | 0.17567 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ12 | 3 | DXGF EL2 | Cooling | Sensible | 8115.46 | 0.47569 | 0.47569 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL2 | Heating | Sensible | 6377.57 | 0.17581 | 0.17581 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ13 | 1 | DXGF EL1 | Cooling | Sensible | 8884.13 | 0.51893 | 0.51893 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL1 | Heating | Sensible | 6129.53 | 0.17081 | 0.17081 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ13 | 3 | DXGF EL2 | Cooling | Sensible | 9350.58 | 0.57174 | 0.57174 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL2 | Heating | Sensible | 6122.71 | 0.17062 | 0.17062 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 1 | DXGF EL1 | Cooling | Sensible | 8511.58 | 0.47812 | 0.47812 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL1 | Heating | Sensible | 7537.4 | 0.24293 | 0.24293 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 3 | DXGF EL2 | Cooling | Sensible | 8579.52 | 0.48194 | 0.48194 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL2 | Heating | Sensible | 7532.51 | 0.24277 | 0.24277 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ15 | 1 | DXGF EL1 | Cooling | Sensible | 10860.35 | 0.61866 | 0.61866 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL1 | Heating | Sensible | 6496.97 | 0.18523 | 0.18523 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL2 | Cooling | Sensible | 11216.29 | 0.66796 | 0.66796 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL2 | Heating | Sensible | 6494.09 | 0.18515 | 0.18515 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL1 | Cooling | Sensible | 8239.72 | 0.55403 | 0.55403 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL1 | Heating | Sensible | 6835.19 | 0.18489 | 0.18489 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL2 | Cooling | Sensible | 8991.75 | 0.63248 | 0.63248 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL2 | Heating | Sensible | 6828.3 | 0.1847 | 0.1847 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 4449.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 5578.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 6128.3 | 6128.3 | 6.73 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 7683.7 | 7683.7 | 6.73 | 4
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 8963.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9168.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 12346.7 | 12346.7 | 6.73 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 12628.9 | 12628.9 | 6.71 | 4
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10628.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10407.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 14639.4 | 14639.4 | 6.77 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 14335.1 | 14335.1 | 6.79 | 4
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 8793.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9434.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 12112.2 | 12112.2 | 6.74 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 12994.7 | 12994.7 | 6.69 | 4
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10656.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10734.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 14678.6 | 14678.6 | 6.77 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 14786.4 | 14786.4 | 6.76 | 4
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9027.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10005.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 12434.1 | 12434.1 | 6.72 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 13782.1 | 13782.1 | 6.82 | 4
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10435.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 11704.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 14374.3 | 14374.3 | 6.78 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 16121.6 | 16121.6 | 6.84 | 4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9842.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10864.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 13557.2 | 13557.2 | 6.83 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 14965.5 | 14965.5 | 6.75 | 4
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 13600.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 14181.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 18733.3 | 18733.3 | 6.72 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 19534.4 | 19534.4 | 6.81 | 4
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9652.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9788.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 13294.9 | 13294.9 | 6.85 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 13482.3 | 13482.3 | 6.84 | 4
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 13224 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 14609.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 18215 | 18215 | 6.74 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 20122.8 | 20122.8 | 6.78 | 4
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 11546.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 11345.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 15903.8 | 15903.8 | 6.7 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 15627.2 | 15627.2 | 6.72 | 4
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 12376.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 13636.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 17047.7 | 17047.7 | 6.79 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 18782.5 | 18782.5 | 6.72 | 4
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 11403.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 11494.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 15706.9 | 15706.9 | 6.71 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 15832.4 | 15832.4 | 6.71 | 4
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 14755.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15930.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 20324.1 | 20324.1 | 6.77 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 21943.4 | 21943.4 | 6.71 | 4
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 13213.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15084.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 18200.9 | 18200.9 | 6.74 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 20778.1 | 20778.1 | 6.76 | 4
DX Heating Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 6128.3 | 6128.3 | 6.73 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 7683.7 | 7683.7 | 6.73 | 4
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 12346.7 | 12346.7 | 6.73 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 12628.9 | 12628.9 | 6.71 | 4
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 14639.4 | 14639.4 | 6.77 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 14335.1 | 14335.1 | 6.79 | 4
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 12112.2 | 12112.2 | 6.74 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 12994.7 | 12994.7 | 6.69 | 4
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 14678.6 | 14678.6 | 6.77 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 14786.4 | 14786.4 | 6.76 | 4
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 12434.1 | 12434.1 | 6.72 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 13782.1 | 13782.1 | 6.82 | 4
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 14374.3 | 14374.3 | 6.78 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 16121.6 | 16121.6 | 6.84 | 4
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 13557.2 | 13557.2 | 6.83 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 14965.5 | 14965.5 | 6.75 | 4
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 18733.3 | 18733.3 | 6.72 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 19534.4 | 19534.4 | 6.81 | 4
CZ10 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 13294.9 | 13294.9 | 6.85 | 4
CZ10 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 13482.3 | 13482.3 | 6.84 | 4
CZ11 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 18215 | 18215 | 6.74 | 4
CZ11 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 20122.8 | 20122.8 | 6.78 | 4
CZ12 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 15903.8 | 15903.8 | 6.7 | 4
CZ12 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 15627.2 | 15627.2 | 6.72 | 4
CZ13 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 17047.7 | 17047.7 | 6.79 | 4
CZ13 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 18782.5 | 18782.5 | 6.72 | 4
CZ14 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 15706.9 | 15706.9 | 6.71 | 4
CZ14 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 15832.4 | 15832.4 | 6.71 | 4
CZ15 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 20324.1 | 20324.1 | 6.77 | 4
CZ15 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 21943.4 | 21943.4 | 6.71 | 4
CZ16 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL1 HEATING COIL | 18200.9 | 18200.9 | 6.74 | 4
CZ16 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 20778.1 | 20778.1 | 6.76 | 4
SWHC049-03 SEER Rated AC HP_SFm_1975 | SFm&2&rDXHP&Ex&dxHP_equip | HSPF_7p0_SEER_13_Pre
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL2 | Cooling | Sensible | 8757.1 | 0.67276 | 0.67276 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL2 | Heating | Sensible | 10373.59 | 0.24155 | 0.24155 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ01 | 3 | DXGF EL5 | Cooling | Sensible | 7019.22 | 0.53924 | 0.53924 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL5 | Heating | Sensible | 10131.76 | 0.23592 | 0.23592 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ02 | 1 | DXGF EL2 | Cooling | Sensible | 16860.87 | 0.93794 | 0.93794 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL2 | Heating | Sensible | 14744.55 | 0.38147 | 0.38147 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ02 | 3 | DXGF EL5 | Cooling | Sensible | 15351.01 | 0.8538 | 0.8538 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL5 | Heating | Sensible | 14512.95 | 0.37548 | 0.37548 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ03 | 1 | DXGF EL2 | Cooling | Sensible | 16650.69 | 1.1608 | 1.1608 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL2 | Heating | Sensible | 12118.9 | 0.31719 | 0.31719 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ03 | 3 | DXGF EL5 | Cooling | Sensible | 14674.81 | 1.0231 | 1.0231 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL5 | Heating | Sensible | 11997.55 | 0.31401 | 0.31401 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 1 | DXGF EL2 | Cooling | Sensible | 16609.66 | 0.94284 | 0.94284 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL2 | Heating | Sensible | 12719.55 | 0.33247 | 0.33247 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 3 | DXGF EL5 | Cooling | Sensible | 14761.68 | 0.8246 | 0.8246 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL5 | Heating | Sensible | 12477.64 | 0.32615 | 0.32615 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 1 | DXGF EL2 | Cooling | Sensible | 17337.62 | 1.2152 | 1.2152 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL2 | Heating | Sensible | 13992.69 | 0.36823 | 0.36823 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 3 | DXGF EL5 | Cooling | Sensible | 15066.63 | 1.0561 | 1.0561 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL5 | Heating | Sensible | 13850.89 | 0.3645 | 0.3645 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ06 | 1 | DXGF EL2 | Cooling | Sensible | 14830.64 | 0.99679 | 0.99679 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL2 | Heating | Sensible | 7167.48 | 0.17979 | 0.17979 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:20
CZ06 | 3 | DXGF EL5 | Cooling | Sensible | 12576.53 | 0.84528 | 0.84528 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL5 | Heating | Sensible | 7017.79 | 0.17604 | 0.17604 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:20
CZ07 | 1 | DXGF EL2 | Cooling | Sensible | 15893.48 | 1.0089 | 1.0089 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL2 | Heating | Sensible | 6174.78 | 0.14827 | 0.14827 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 3 | DXGF EL5 | Cooling | Sensible | 13401.63 | 0.83717 | 0.83717 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL5 | Heating | Sensible | 6032.26 | 0.14485 | 0.14485 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 1 | DXGF EL2 | Cooling | Sensible | 16527.28 | 0.97035 | 0.97035 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL2 | Heating | Sensible | 7039.26 | 0.16911 | 0.16911 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 3 | DXGF EL5 | Cooling | Sensible | 13720.25 | 0.78043 | 0.78043 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL5 | Heating | Sensible | 6865.31 | 0.16493 | 0.16493 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ09 | 1 | DXGF EL2 | Cooling | Sensible | 20799.74 | 1.3226 | 1.3226 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL2 | Heating | Sensible | 13654.27 | 0.37725 | 0.37725 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL5 | Cooling | Sensible | 17313.25 | 1.1515 | 1.1515 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL5 | Heating | Sensible | 13458.06 | 0.37184 | 0.37184 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 16045.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12861 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 22101.2 | 22101.2 | 6.82 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 17714.9 | 17714.9 | 6.76 | 4
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 22370 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 20363.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30812.8 | 30812.8 | 6.8 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 28048.6 | 28048.6 | 6.8 | 4
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 27685.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 24400.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 38134.5 | 38134.5 | 6.77 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 33609.2 | 33609.2 | 6.73 | 4
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 22486.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 19666.8 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30973.8 | 30973.8 | 6.8 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 27089.3 | 27089.3 | 6.75 | 4
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 28983.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 25187.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 39922.8 | 39922.8 | 6.73 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 34693.4 | 34693.4 | 6.71 | 4
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 23773.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 20160.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 32746 | 32746 | 6.75 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 27769 | 27769 | 6.73 | 4
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 24063.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 19966.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 33145.3 | 33145.3 | 6.75 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 27502.3 | 27502.3 | 6.73 | 4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 23143 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 18613.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 31877.5 | 31877.5 | 6.78 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25638.5 | 25638.5 | 6.79 | 4
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 31544.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 27464.6 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 43450.1 | 43450.1 | 6.67 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 37830 | 37830 | 6.77 | 4
DX Heating Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 22101.2 | 22101.2 | 6.82 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 17714.9 | 17714.9 | 6.76 | 4
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30812.8 | 30812.8 | 6.8 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 28048.6 | 28048.6 | 6.8 | 4
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 38134.5 | 38134.5 | 6.77 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 33609.2 | 33609.2 | 6.73 | 4
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 30973.8 | 30973.8 | 6.8 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 27089.3 | 27089.3 | 6.75 | 4
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 39922.8 | 39922.8 | 6.73 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 34693.4 | 34693.4 | 6.71 | 4
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 32746 | 32746 | 6.75 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 27769 | 27769 | 6.73 | 4
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 33145.3 | 33145.3 | 6.75 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 27502.3 | 27502.3 | 6.73 | 4
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 31877.5 | 31877.5 | 6.78 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 25638.5 | 25638.5 | 6.79 | 4
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL2 HEATING COIL | 43450.1 | 43450.1 | 6.67 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL5 HEATING COIL | 37830 | 37830 | 6.77 | 4
SWHC049-03 SEER Rated AC HP_SFm_1975 | SFm&2&rDXGF&Ex&dxAC_equip | dxAC-Res-SEER-13.0
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL2 | Cooling | Sensible | 8725.79 | 0.67035 | 0.67035 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL2 | Heating | Sensible | 10249.24 | 0.23865 | 0.23865 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ01 | 3 | DXGF EL5 | Cooling | Sensible | 6983.28 | 0.53648 | 0.53648 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL5 | Heating | Sensible | 10035.46 | 0.23368 | 0.23368 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ02 | 1 | DXGF EL2 | Cooling | Sensible | 16771.54 | 0.93308 | 0.93308 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL2 | Heating | Sensible | 14640.43 | 0.37877 | 0.37877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ02 | 3 | DXGF EL5 | Cooling | Sensible | 15272.2 | 0.84937 | 0.84937 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL5 | Heating | Sensible | 14436.87 | 0.37351 | 0.37351 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ03 | 1 | DXGF EL2 | Cooling | Sensible | 16607.9 | 1.1578 | 1.1578 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL2 | Heating | Sensible | 12058.04 | 0.3156 | 0.3156 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ03 | 3 | DXGF EL5 | Cooling | Sensible | 14636.98 | 1.0204 | 1.0204 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL5 | Heating | Sensible | 11952.53 | 0.31283 | 0.31283 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 1 | DXGF EL2 | Cooling | Sensible | 16476.75 | 0.93568 | 0.93568 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL2 | Heating | Sensible | 12621.11 | 0.3299 | 0.3299 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 3 | DXGF EL5 | Cooling | Sensible | 14641.84 | 0.81779 | 0.81779 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL5 | Heating | Sensible | 12407.86 | 0.32433 | 0.32433 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 1 | DXGF EL2 | Cooling | Sensible | 17296.38 | 1.2124 | 1.2124 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL2 | Heating | Sensible | 13921.39 | 0.36635 | 0.36635 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 3 | DXGF EL5 | Cooling | Sensible | 15029.83 | 1.0535 | 1.0535 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL5 | Heating | Sensible | 13798.07 | 0.36311 | 0.36311 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ06 | 1 | DXGF EL2 | Cooling | Sensible | 14728.32 | 0.98991 | 0.98991 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL2 | Heating | Sensible | 7098.61 | 0.17806 | 0.17806 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:20
CZ06 | 3 | DXGF EL5 | Cooling | Sensible | 12481 | 0.83886 | 0.83886 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL5 | Heating | Sensible | 6966.89 | 0.17476 | 0.17476 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 1 | DXGF EL2 | Cooling | Sensible | 15776.25 | 1.0012 | 1.0012 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL2 | Heating | Sensible | 6101.66 | 0.14651 | 0.14651 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 3 | DXGF EL5 | Cooling | Sensible | 13288.43 | 0.8301 | 0.8301 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL5 | Heating | Sensible | 5976.5 | 0.14351 | 0.14351 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 1 | DXGF EL2 | Cooling | Sensible | 16396.72 | 0.96216 | 0.96216 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL2 | Heating | Sensible | 6952.63 | 0.16703 | 0.16703 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 3 | DXGF EL5 | Cooling | Sensible | 13595.41 | 0.77291 | 0.77291 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL5 | Heating | Sensible | 6799.27 | 0.16334 | 0.16334 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ09 | 1 | DXGF EL2 | Cooling | Sensible | 20656.58 | 1.3132 | 1.3132 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL2 | Heating | Sensible | 13581.25 | 0.37524 | 0.37524 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL5 | Cooling | Sensible | 17180.75 | 1.1427 | 1.1427 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL5 | Heating | Sensible | 13409.69 | 0.3705 | 0.3705 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10485 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 8391.1 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 17239.2 | 2.72 | 9.27 | 10.5 | 9.93 | 10.31
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15700.6 | 2.72 | 9.27 | 10.5 | 9.93 | 10.31
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18109.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15960.5 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 16959.2 | 2.71 | 9.25 | 10.47 | 9.9 | 10.26
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15097.1 | 2.72 | 9.27 | 10.5 | 9.93 | 10.31
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18962.5 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16477.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15483.2 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 13120.7 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 16367.1 | 2.67 | 9.1 | 10.28 | 9.73 | 9.99
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 13821 | 2.67 | 9.12 | 10.32 | 9.76 | 10.04
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 17095.7 | 2.7 | 9.22 | 10.43 | 9.87 | 10.21
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14183.8 | 2.71 | 9.26 | 10.49 | 9.92 | 10.3
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 21517.1 | 2.67 | 9.1 | 10.29 | 9.73 | 10
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 17957.3 | 2.65 | 9.04 | 10.21 | 9.66 | 9.88
SWHC049-03 SEER Rated AC HP_SFm_1975 | SFm&1&rDXHP&Ex&dxHP_equip | HSPF_7p0_SEER_13_Pre
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL7 | Cooling | Sensible | 920.68 | 0.0707 | 0.0707 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL7 | Heating | Sensible | 5241.48 | 0.12205 | 0.12205 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ01 | 3 | DXGF EL8 | Cooling | Sensible | 1468.69 | 0.11283 | 0.11283 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL8 | Heating | Sensible | 5009.84 | 0.11666 | 0.11666 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ02 | 1 | DXGF EL7 | Cooling | Sensible | 5288.34 | 0.29753 | 0.29753 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL7 | Heating | Sensible | 7923.15 | 0.20499 | 0.20499 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ02 | 3 | DXGF EL8 | Cooling | Sensible | 5759.73 | 0.32469 | 0.32469 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL8 | Heating | Sensible | 7697 | 0.19914 | 0.19914 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ03 | 1 | DXGF EL7 | Cooling | Sensible | 4904.11 | 0.34189 | 0.34189 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL7 | Heating | Sensible | 6424.18 | 0.16814 | 0.16814 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL8 | Cooling | Sensible | 5459.23 | 0.38059 | 0.38059 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL8 | Heating | Sensible | 6304.36 | 0.165 | 0.165 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL7 | Cooling | Sensible | 5407.86 | 0.30802 | 0.30802 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL7 | Heating | Sensible | 6797.48 | 0.17768 | 0.17768 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL8 | Cooling | Sensible | 6046.15 | 0.34964 | 0.34964 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL8 | Heating | Sensible | 6566.73 | 0.17165 | 0.17165 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL7 | Cooling | Sensible | 5176.64 | 0.36285 | 0.36285 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL7 | Heating | Sensible | 7460.58 | 0.19633 | 0.19633 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 3 | DXGF EL8 | Cooling | Sensible | 5835.23 | 0.40901 | 0.40901 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL8 | Heating | Sensible | 7320.48 | 0.19264 | 0.19264 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 1 | DXGF EL7 | Cooling | Sensible | 4388.8 | 0.29498 | 0.29498 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL7 | Heating | Sensible | 3693.37 | 0.0926 | 0.0926 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL8 | Cooling | Sensible | 4912.84 | 0.3302 | 0.3302 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL8 | Heating | Sensible | 3550.19 | 0.0891 | 0.0891 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL7 | Cooling | Sensible | 5302.39 | 0.35104 | 0.35104 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL7 | Heating | Sensible | 3073.46 | 0.0738 | 0.0738 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXGF EL8 | Cooling | Sensible | 6032.21 | 0.3959 | 0.3959 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL8 | Heating | Sensible | 2936.67 | 0.0705 | 0.0705 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXGF EL7 | Cooling | Sensible | 5802.1 | 0.36782 | 0.36782 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL7 | Heating | Sensible | 3593.96 | 0.0863 | 0.0863 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 3 | DXGF EL8 | Cooling | Sensible | 6232.58 | 0.38025 | 0.38025 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL8 | Heating | Sensible | 3427.22 | 0.0823 | 0.0823 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXGF EL7 | Cooling | Sensible | 7928.66 | 0.52735 | 0.52735 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL7 | Heating | Sensible | 7228.64 | 0.19987 | 0.19987 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL8 | Cooling | Sensible | 8334.04 | 0.5413 | 0.5413 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL8 | Heating | Sensible | 7045.35 | 0.19481 | 0.19481 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2910.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3593.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4009.5 | 4009.5 | 6.84 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 4949.4 | 4949.4 | 6.68 | 4
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 7096.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 7743.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9774.3 | 9774.3 | 6.81 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10666.6 | 10666.6 | 6.74 | 4
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 8154.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 9077.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 11231.7 | 11231.7 | 6.8 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 12503.1 | 12503.1 | 6.72 | 4
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 7346.2 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 8338.9 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 10118.8 | 10118.8 | 6.78 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 11486.1 | 11486.1 | 6.78 | 4
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 8654 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 9755 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 11920.1 | 11920.1 | 6.75 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 13436.6 | 13436.6 | 6.84 | 4
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 7035.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 7875.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9690.5 | 9690.5 | 6.81 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10847.6 | 10847.6 | 6.72 | 4
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 8372.4 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 9442.3 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 11532.2 | 11532.2 | 6.78 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 13005.9 | 13005.9 | 6.69 | 4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 8772.7 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 9069.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 12083.6 | 12083.6 | 6.74 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 12491.9 | 12491.9 | 6.72 | 4
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 12577.5 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 12910.1 | 2.81 | 9.6 | 10.9 | 10.31 | 10.93
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 17324.4 | 17324.4 | 6.78 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 17782.6 | 17782.6 | 6.76 | 4
DX Heating Coil Standard Rating Information
CZ |  | Component Type | Component Name | High Temperature Heating (net) Rating Capacity {W} | Low Temperature Heating (net) Rating Capacity {W} | HSPF {Btu/W-h} | Region Number
CZ01 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 4009.5 | 4009.5 | 6.84 | 4
CZ01 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 4949.4 | 4949.4 | 6.68 | 4
CZ02 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9774.3 | 9774.3 | 6.81 | 4
CZ02 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10666.6 | 10666.6 | 6.74 | 4
CZ03 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 11231.7 | 11231.7 | 6.8 | 4
CZ03 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 12503.1 | 12503.1 | 6.72 | 4
CZ04 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 10118.8 | 10118.8 | 6.78 | 4
CZ04 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 11486.1 | 11486.1 | 6.78 | 4
CZ05 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 11920.1 | 11920.1 | 6.75 | 4
CZ05 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 13436.6 | 13436.6 | 6.84 | 4
CZ06 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 9690.5 | 9690.5 | 6.81 | 4
CZ06 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 10847.6 | 10847.6 | 6.72 | 4
CZ07 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 11532.2 | 11532.2 | 6.78 | 4
CZ07 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 13005.9 | 13005.9 | 6.69 | 4
CZ08 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 12083.6 | 12083.6 | 6.74 | 4
CZ08 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 12491.9 | 12491.9 | 6.72 | 4
CZ09 | 1 | Coil:Heating:DX:SingleSpeed | DXHP EL7 HEATING COIL | 17324.4 | 17324.4 | 6.78 | 4
CZ09 | 2 | Coil:Heating:DX:SingleSpeed | DXHP EL8 HEATING COIL | 17782.6 | 17782.6 | 6.76 | 4
SWHC049-03 SEER Rated AC HP_SFm_1975 | SFm&1&rDXGF&Ex&dxAC_equip | dxAC-Res-SEER-13.0
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL7 | Cooling | Sensible | 920.68 | 0.0707 | 0.0707 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL7 | Heating | Sensible | 5241.48 | 0.12205 | 0.12205 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ01 | 3 | DXGF EL8 | Cooling | Sensible | 1468.69 | 0.11283 | 0.11283 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL8 | Heating | Sensible | 5009.84 | 0.11666 | 0.11666 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ02 | 1 | DXGF EL7 | Cooling | Sensible | 5288.34 | 0.29753 | 0.29753 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL7 | Heating | Sensible | 7923.15 | 0.20499 | 0.20499 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ02 | 3 | DXGF EL8 | Cooling | Sensible | 5759.73 | 0.32469 | 0.32469 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL8 | Heating | Sensible | 7697 | 0.19914 | 0.19914 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ03 | 1 | DXGF EL7 | Cooling | Sensible | 4904.11 | 0.34189 | 0.34189 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL7 | Heating | Sensible | 6424.18 | 0.16814 | 0.16814 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL8 | Cooling | Sensible | 5459.23 | 0.38059 | 0.38059 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL8 | Heating | Sensible | 6304.36 | 0.165 | 0.165 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL7 | Cooling | Sensible | 5407.86 | 0.30802 | 0.30802 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL7 | Heating | Sensible | 6797.48 | 0.17768 | 0.17768 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL8 | Cooling | Sensible | 6046.15 | 0.34964 | 0.34964 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL8 | Heating | Sensible | 6566.73 | 0.17165 | 0.17165 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL7 | Cooling | Sensible | 5176.64 | 0.36285 | 0.36285 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL7 | Heating | Sensible | 7460.58 | 0.19633 | 0.19633 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 3 | DXGF EL8 | Cooling | Sensible | 5835.23 | 0.40901 | 0.40901 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL8 | Heating | Sensible | 7320.48 | 0.19264 | 0.19264 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 1 | DXGF EL7 | Cooling | Sensible | 4388.8 | 0.29498 | 0.29498 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL7 | Heating | Sensible | 3693.37 | 0.0926 | 0.0926 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL8 | Cooling | Sensible | 4912.84 | 0.3302 | 0.3302 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL8 | Heating | Sensible | 3550.19 | 0.0891 | 0.0891 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL7 | Cooling | Sensible | 5302.39 | 0.35104 | 0.35104 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL7 | Heating | Sensible | 3073.46 | 0.0738 | 0.0738 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXGF EL8 | Cooling | Sensible | 6032.21 | 0.3959 | 0.3959 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL8 | Heating | Sensible | 2936.67 | 0.0705 | 0.0705 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXGF EL7 | Cooling | Sensible | 5802.1 | 0.36782 | 0.36782 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL7 | Heating | Sensible | 3593.96 | 0.0863 | 0.0863 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 3 | DXGF EL8 | Cooling | Sensible | 6232.58 | 0.38025 | 0.38025 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL8 | Heating | Sensible | 3427.22 | 0.0823 | 0.0823 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXGF EL7 | Cooling | Sensible | 7928.66 | 0.52735 | 0.52735 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL7 | Heating | Sensible | 7228.64 | 0.19987 | 0.19987 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL8 | Cooling | Sensible | 8334.04 | 0.5413 | 0.5413 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL8 | Heating | Sensible | 7045.35 | 0.19481 | 0.19481 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 1909 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 2356.5 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5443.2 | 2.71 | 9.26 | 10.48 | 9.92 | 10.29
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5919.3 | 2.71 | 9.25 | 10.48 | 9.91 | 10.28
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5347.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5952.9 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5585.4 | 2.71 | 9.25 | 10.47 | 9.9 | 10.27
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6239.9 | 2.7 | 9.22 | 10.44 | 9.88 | 10.22
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5675.3 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6397.3 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4613.8 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5164.6 | 2.65 | 9.03 | 10.2 | 9.65 | 9.87
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5618.9 | 2.66 | 9.06 | 10.24 | 9.69 | 9.93
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6349.8 | 2.66 | 9.07 | 10.25 | 9.69 | 9.94
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 6117.8 | 2.67 | 9.12 | 10.31 | 9.76 | 10.04
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6537.9 | 2.69 | 9.17 | 10.37 | 9.81 | 10.13
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 8286.3 | 2.65 | 9.04 | 10.21 | 9.66 | 9.88
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 8695 | 2.66 | 9.07 | 10.25 | 9.7 | 9.94
SWHC031-03 Furnace_SFm_1975 | SFm&1&rNCGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL7 | Cooling | Sensible | 920.68 | 0.0707 | 0.0707 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL7 | Heating | Sensible | 5241.48 | 0.12205 | 0.12205 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ01 | 3 | DXGF EL8 | Cooling | Sensible | 1468.69 | 0.11283 | 0.11283 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL8 | Heating | Sensible | 5009.84 | 0.11666 | 0.11666 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ02 | 1 | DXGF EL7 | Cooling | Sensible | 5288.34 | 0.29753 | 0.29753 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL7 | Heating | Sensible | 7923.15 | 0.20499 | 0.20499 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ02 | 3 | DXGF EL8 | Cooling | Sensible | 5759.73 | 0.32469 | 0.32469 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL8 | Heating | Sensible | 7697 | 0.19914 | 0.19914 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ03 | 1 | DXGF EL7 | Cooling | Sensible | 4904.11 | 0.34189 | 0.34189 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL7 | Heating | Sensible | 6424.18 | 0.16814 | 0.16814 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL8 | Cooling | Sensible | 5459.23 | 0.38059 | 0.38059 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL8 | Heating | Sensible | 6304.36 | 0.165 | 0.165 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL7 | Cooling | Sensible | 5407.86 | 0.30802 | 0.30802 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL7 | Heating | Sensible | 6797.48 | 0.17768 | 0.17768 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL8 | Cooling | Sensible | 6046.15 | 0.34964 | 0.34964 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL8 | Heating | Sensible | 6566.73 | 0.17165 | 0.17165 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL7 | Cooling | Sensible | 5176.64 | 0.36285 | 0.36285 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL7 | Heating | Sensible | 7460.58 | 0.19633 | 0.19633 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 3 | DXGF EL8 | Cooling | Sensible | 5835.23 | 0.40901 | 0.40901 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL8 | Heating | Sensible | 7320.48 | 0.19264 | 0.19264 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 1 | DXGF EL7 | Cooling | Sensible | 4388.8 | 0.29498 | 0.29498 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL7 | Heating | Sensible | 3693.37 | 0.0926 | 0.0926 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL8 | Cooling | Sensible | 4912.84 | 0.3302 | 0.3302 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL8 | Heating | Sensible | 3550.19 | 0.0891 | 0.0891 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL7 | Cooling | Sensible | 5302.39 | 0.35104 | 0.35104 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL7 | Heating | Sensible | 3073.46 | 0.0738 | 0.0738 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXGF EL8 | Cooling | Sensible | 6032.21 | 0.3959 | 0.3959 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL8 | Heating | Sensible | 2936.67 | 0.0705 | 0.0705 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXGF EL7 | Cooling | Sensible | 5802.1 | 0.36782 | 0.36782 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL7 | Heating | Sensible | 3593.96 | 0.0863 | 0.0863 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 3 | DXGF EL8 | Cooling | Sensible | 6232.58 | 0.38025 | 0.38025 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL8 | Heating | Sensible | 3427.22 | 0.0823 | 0.0823 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXGF EL7 | Cooling | Sensible | 7928.66 | 0.52735 | 0.52735 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL7 | Heating | Sensible | 7228.64 | 0.19987 | 0.19987 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL8 | Cooling | Sensible | 8334.04 | 0.5413 | 0.5413 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL8 | Heating | Sensible | 7045.35 | 0.19481 | 0.19481 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
SWHC031-03 Furnace_SFm_1975 | SFm&1&rDXGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL7 | Cooling | Sensible | 920.68 | 0.0707 | 0.0707 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL7 | Heating | Sensible | 5241.48 | 0.12205 | 0.12205 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ01 | 3 | DXGF EL8 | Cooling | Sensible | 1468.69 | 0.11283 | 0.11283 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL8 | Heating | Sensible | 5009.84 | 0.11666 | 0.11666 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ02 | 1 | DXGF EL7 | Cooling | Sensible | 5288.34 | 0.29753 | 0.29753 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL7 | Heating | Sensible | 7923.15 | 0.20499 | 0.20499 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ02 | 3 | DXGF EL8 | Cooling | Sensible | 5759.73 | 0.32469 | 0.32469 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL8 | Heating | Sensible | 7697 | 0.19914 | 0.19914 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ03 | 1 | DXGF EL7 | Cooling | Sensible | 4904.11 | 0.34189 | 0.34189 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL7 | Heating | Sensible | 6424.18 | 0.16814 | 0.16814 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ03 | 3 | DXGF EL8 | Cooling | Sensible | 5459.23 | 0.38059 | 0.38059 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL8 | Heating | Sensible | 6304.36 | 0.165 | 0.165 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 1 | DXGF EL7 | Cooling | Sensible | 5407.86 | 0.30802 | 0.30802 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL7 | Heating | Sensible | 6797.48 | 0.17768 | 0.17768 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ04 | 3 | DXGF EL8 | Cooling | Sensible | 6046.15 | 0.34964 | 0.34964 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL8 | Heating | Sensible | 6566.73 | 0.17165 | 0.17165 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 1 | DXGF EL7 | Cooling | Sensible | 5176.64 | 0.36285 | 0.36285 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL7 | Heating | Sensible | 7460.58 | 0.19633 | 0.19633 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ05 | 3 | DXGF EL8 | Cooling | Sensible | 5835.23 | 0.40901 | 0.40901 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL8 | Heating | Sensible | 7320.48 | 0.19264 | 0.19264 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 1 | DXGF EL7 | Cooling | Sensible | 4388.8 | 0.29498 | 0.29498 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL7 | Heating | Sensible | 3693.37 | 0.0926 | 0.0926 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 3 | DXGF EL8 | Cooling | Sensible | 4912.84 | 0.3302 | 0.3302 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL8 | Heating | Sensible | 3550.19 | 0.0891 | 0.0891 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXGF EL7 | Cooling | Sensible | 5302.39 | 0.35104 | 0.35104 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL7 | Heating | Sensible | 3073.46 | 0.0738 | 0.0738 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXGF EL8 | Cooling | Sensible | 6032.21 | 0.3959 | 0.3959 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL8 | Heating | Sensible | 2936.67 | 0.0705 | 0.0705 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXGF EL7 | Cooling | Sensible | 5802.1 | 0.36782 | 0.36782 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL7 | Heating | Sensible | 3593.96 | 0.0863 | 0.0863 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 3 | DXGF EL8 | Cooling | Sensible | 6232.58 | 0.38025 | 0.38025 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL8 | Heating | Sensible | 3427.22 | 0.0823 | 0.0823 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXGF EL7 | Cooling | Sensible | 7928.66 | 0.52735 | 0.52735 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL7 | Heating | Sensible | 7228.64 | 0.19987 | 0.19987 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL8 | Cooling | Sensible | 8334.04 | 0.5413 | 0.5413 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL8 | Heating | Sensible | 7045.35 | 0.19481 | 0.19481 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 1925.6 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 2377.1 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5538.6 | 2.78 | 9.5 | 10.08 | 9.53 | 9.72
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6020.6 | 2.78 | 9.49 | 10.07 | 9.53 | 9.71
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5394.3 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6004.8 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5686.1 | 2.78 | 9.49 | 10.07 | 9.52 | 9.7
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6353.5 | 2.77 | 9.47 | 10.04 | 9.5 | 9.66
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5724.9 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6453.2 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4654 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5209.7 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5693.8 | 2.72 | 9.29 | 9.85 | 9.32 | 9.4
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6434.1 | 2.72 | 9.3 | 9.86 | 9.32 | 9.4
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 6245.5 | 2.74 | 9.36 | 9.93 | 9.39 | 9.51
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6663.8 | 2.76 | 9.41 | 9.98 | 9.44 | 9.58
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 8542.3 | 2.72 | 9.29 | 9.85 | 9.32 | 9.39
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 8948.7 | 2.73 | 9.32 | 9.89 | 9.35 | 9.44
SWHC031-03 Furnace_SFm_1975 | SFm&2&rNCGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL2 | Cooling | Sensible | 8725.79 | 0.67035 | 0.67035 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL2 | Heating | Sensible | 10249.24 | 0.23865 | 0.23865 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ01 | 3 | DXGF EL5 | Cooling | Sensible | 6983.28 | 0.53648 | 0.53648 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL5 | Heating | Sensible | 10035.46 | 0.23368 | 0.23368 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ02 | 1 | DXGF EL2 | Cooling | Sensible | 16771.54 | 0.93308 | 0.93308 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL2 | Heating | Sensible | 14640.43 | 0.37877 | 0.37877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ02 | 3 | DXGF EL5 | Cooling | Sensible | 15272.2 | 0.84937 | 0.84937 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL5 | Heating | Sensible | 14436.87 | 0.37351 | 0.37351 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ03 | 1 | DXGF EL2 | Cooling | Sensible | 16607.9 | 1.1578 | 1.1578 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL2 | Heating | Sensible | 12058.04 | 0.3156 | 0.3156 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ03 | 3 | DXGF EL5 | Cooling | Sensible | 14636.98 | 1.0204 | 1.0204 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL5 | Heating | Sensible | 11952.53 | 0.31283 | 0.31283 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 1 | DXGF EL2 | Cooling | Sensible | 16476.75 | 0.93568 | 0.93568 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL2 | Heating | Sensible | 12621.11 | 0.3299 | 0.3299 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 3 | DXGF EL5 | Cooling | Sensible | 14641.84 | 0.81779 | 0.81779 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL5 | Heating | Sensible | 12407.86 | 0.32433 | 0.32433 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 1 | DXGF EL2 | Cooling | Sensible | 17296.38 | 1.2124 | 1.2124 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL2 | Heating | Sensible | 13921.39 | 0.36635 | 0.36635 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 3 | DXGF EL5 | Cooling | Sensible | 15029.83 | 1.0535 | 1.0535 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL5 | Heating | Sensible | 13798.07 | 0.36311 | 0.36311 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ06 | 1 | DXGF EL2 | Cooling | Sensible | 14728.32 | 0.98991 | 0.98991 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL2 | Heating | Sensible | 7098.61 | 0.17806 | 0.17806 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:20
CZ06 | 3 | DXGF EL5 | Cooling | Sensible | 12481 | 0.83886 | 0.83886 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL5 | Heating | Sensible | 6966.89 | 0.17476 | 0.17476 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 1 | DXGF EL2 | Cooling | Sensible | 15776.25 | 1.0012 | 1.0012 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL2 | Heating | Sensible | 6101.66 | 0.14651 | 0.14651 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 3 | DXGF EL5 | Cooling | Sensible | 13288.43 | 0.8301 | 0.8301 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL5 | Heating | Sensible | 5976.5 | 0.14351 | 0.14351 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 1 | DXGF EL2 | Cooling | Sensible | 16396.72 | 0.96216 | 0.96216 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL2 | Heating | Sensible | 6952.63 | 0.16703 | 0.16703 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 3 | DXGF EL5 | Cooling | Sensible | 13595.41 | 0.77291 | 0.77291 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL5 | Heating | Sensible | 6799.27 | 0.16334 | 0.16334 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ09 | 1 | DXGF EL2 | Cooling | Sensible | 20656.58 | 1.3132 | 1.3132 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL2 | Heating | Sensible | 13581.25 | 0.37524 | 0.37524 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL5 | Cooling | Sensible | 17180.75 | 1.1427 | 1.1427 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL5 | Heating | Sensible | 13409.69 | 0.3705 | 0.3705 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
SWHC031-03 Furnace_SFm_1975 | SFm&2&rDXGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL2 | Cooling | Sensible | 8725.79 | 0.67035 | 0.67035 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL2 | Heating | Sensible | 10249.24 | 0.23865 | 0.23865 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ01 | 3 | DXGF EL5 | Cooling | Sensible | 6983.28 | 0.53648 | 0.53648 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL5 | Heating | Sensible | 10035.46 | 0.23368 | 0.23368 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ02 | 1 | DXGF EL2 | Cooling | Sensible | 16771.54 | 0.93308 | 0.93308 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL2 | Heating | Sensible | 14640.43 | 0.37877 | 0.37877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ02 | 3 | DXGF EL5 | Cooling | Sensible | 15272.2 | 0.84937 | 0.84937 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL5 | Heating | Sensible | 14436.87 | 0.37351 | 0.37351 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 14:10
CZ03 | 1 | DXGF EL2 | Cooling | Sensible | 16607.9 | 1.1578 | 1.1578 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL2 | Heating | Sensible | 12058.04 | 0.3156 | 0.3156 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ03 | 3 | DXGF EL5 | Cooling | Sensible | 14636.98 | 1.0204 | 1.0204 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL5 | Heating | Sensible | 11952.53 | 0.31283 | 0.31283 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 1 | DXGF EL2 | Cooling | Sensible | 16476.75 | 0.93568 | 0.93568 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL2 | Heating | Sensible | 12621.11 | 0.3299 | 0.3299 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ04 | 3 | DXGF EL5 | Cooling | Sensible | 14641.84 | 0.81779 | 0.81779 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL5 | Heating | Sensible | 12407.86 | 0.32433 | 0.32433 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 1 | DXGF EL2 | Cooling | Sensible | 17296.38 | 1.2124 | 1.2124 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL2 | Heating | Sensible | 13921.39 | 0.36635 | 0.36635 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ05 | 3 | DXGF EL5 | Cooling | Sensible | 15029.83 | 1.0535 | 1.0535 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL5 | Heating | Sensible | 13798.07 | 0.36311 | 0.36311 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ06 | 1 | DXGF EL2 | Cooling | Sensible | 14728.32 | 0.98991 | 0.98991 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL2 | Heating | Sensible | 7098.61 | 0.17806 | 0.17806 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:20
CZ06 | 3 | DXGF EL5 | Cooling | Sensible | 12481 | 0.83886 | 0.83886 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL5 | Heating | Sensible | 6966.89 | 0.17476 | 0.17476 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 1 | DXGF EL2 | Cooling | Sensible | 15776.25 | 1.0012 | 1.0012 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL2 | Heating | Sensible | 6101.66 | 0.14651 | 0.14651 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ07 | 3 | DXGF EL5 | Cooling | Sensible | 13288.43 | 0.8301 | 0.8301 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL5 | Heating | Sensible | 5976.5 | 0.14351 | 0.14351 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 1 | DXGF EL2 | Cooling | Sensible | 16396.72 | 0.96216 | 0.96216 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL2 | Heating | Sensible | 6952.63 | 0.16703 | 0.16703 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ08 | 3 | DXGF EL5 | Cooling | Sensible | 13595.41 | 0.77291 | 0.77291 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL5 | Heating | Sensible | 6799.27 | 0.16334 | 0.16334 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 14:10
CZ09 | 1 | DXGF EL2 | Cooling | Sensible | 20656.58 | 1.3132 | 1.3132 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL2 | Heating | Sensible | 13581.25 | 0.37524 | 0.37524 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL5 | Cooling | Sensible | 17180.75 | 1.1427 | 1.1427 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL5 | Heating | Sensible | 13409.69 | 0.3705 | 0.3705 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10576.5 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 8464.3 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 17539.3 | 2.79 | 9.51 | 10.09 | 9.55 | 9.74
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15973.6 | 2.79 | 9.52 | 10.09 | 9.55 | 9.74
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18267.8 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16099.8 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 17260.5 | 2.78 | 9.49 | 10.06 | 9.52 | 9.7
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15364.8 | 2.79 | 9.51 | 10.09 | 9.55 | 9.74
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 19128 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 16621.5 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15618.4 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 13235.3 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 16565.3 | 2.73 | 9.32 | 9.89 | 9.35 | 9.44
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 13970.4 | 2.74 | 9.35 | 9.92 | 9.38 | 9.48
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 17406.9 | 2.77 | 9.46 | 10.03 | 9.49 | 9.65
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14421.6 | 2.79 | 9.5 | 10.08 | 9.54 | 9.72
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 22112.9 | 2.74 | 9.35 | 9.92 | 9.38 | 9.49
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 18514.7 | 2.72 | 9.29 | 9.85 | 9.32 | 9.39
SWHC031-03 Furnace_DMo | DMo&0&rDXGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL1 | Cooling | Sensible | 2428.32 | 0.18655 | 0.18655 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 2 | DXGF EL1 | Heating | Sensible | 3751.47 | 0.0874 | 0.0874 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ01 | 3 | DXGF EL2 | Cooling | Sensible | 3044.65 | 0.23389 | 0.23389 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXGF EL2 | Heating | Sensible | 3746.03 | 0.0872 | 0.0872 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ02 | 1 | DXGF EL1 | Cooling | Sensible | 6665.45 | 0.37583 | 0.37583 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXGF EL1 | Heating | Sensible | 5400.93 | 0.13973 | 0.13973 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ02 | 3 | DXGF EL2 | Cooling | Sensible | 6809.42 | 0.38442 | 0.38442 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXGF EL2 | Heating | Sensible | 5385.24 | 0.13933 | 0.13933 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ03 | 1 | DXGF EL1 | Cooling | Sensible | 6392.15 | 0.44562 | 0.44562 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXGF EL1 | Heating | Sensible | 4334.93 | 0.11346 | 0.11346 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ03 | 3 | DXGF EL2 | Cooling | Sensible | 6259.28 | 0.43636 | 0.43636 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXGF EL2 | Heating | Sensible | 4329.87 | 0.11333 | 0.11333 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 1 | DXGF EL1 | Cooling | Sensible | 6367.64 | 0.3687 | 0.3687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXGF EL1 | Heating | Sensible | 4598.25 | 0.12019 | 0.12019 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 3 | DXGF EL2 | Cooling | Sensible | 6742.82 | 0.39556 | 0.39556 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXGF EL2 | Heating | Sensible | 4592.43 | 0.12004 | 0.12004 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ05 | 1 | DXGF EL1 | Cooling | Sensible | 6374.55 | 0.44682 | 0.44682 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXGF EL1 | Heating | Sensible | 5152.73 | 0.1356 | 0.1356 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ05 | 3 | DXGF EL2 | Cooling | Sensible | 6421.37 | 0.4501 | 0.4501 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXGF EL2 | Heating | Sensible | 5147.5 | 0.13546 | 0.13546 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ06 | 1 | DXGF EL1 | Cooling | Sensible | 5556.17 | 0.37849 | 0.37849 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXGF EL1 | Heating | Sensible | 2697.81 | 0.0677 | 0.0677 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ06 | 3 | DXGF EL2 | Cooling | Sensible | 6162.84 | 0.41953 | 0.41953 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXGF EL2 | Heating | Sensible | 2692.95 | 0.0676 | 0.0676 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 1 | DXGF EL1 | Cooling | Sensible | 6794.57 | 0.43755 | 0.43755 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXGF EL1 | Heating | Sensible | 2294.96 | 0.0551 | 0.0551 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 3 | DXGF EL2 | Cooling | Sensible | 7412.75 | 0.49074 | 0.49074 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXGF EL2 | Heating | Sensible | 2289.88 | 0.055 | 0.055 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 1 | DXGF EL1 | Cooling | Sensible | 6694.03 | 0.41268 | 0.41268 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXGF EL1 | Heating | Sensible | 2654.94 | 0.0638 | 0.0638 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 3 | DXGF EL2 | Cooling | Sensible | 7593.75 | 0.45555 | 0.45555 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXGF EL2 | Heating | Sensible | 2649.77 | 0.0637 | 0.0637 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ09 | 1 | DXGF EL1 | Cooling | Sensible | 8698.51 | 0.57024 | 0.57024 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXGF EL1 | Heating | Sensible | 5759.41 | 0.15909 | 0.15909 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL2 | Cooling | Sensible | 9537.01 | 0.59463 | 0.59463 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXGF EL2 | Heating | Sensible | 5755.75 | 0.15899 | 0.15899 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL1 | Cooling | Sensible | 7245.53 | 0.40469 | 0.40469 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL1 | Heating | Sensible | 5223.16 | 0.14818 | 0.14818 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ10 | 3 | DXGF EL2 | Cooling | Sensible | 7338.42 | 0.4104 | 0.4104 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL2 | Heating | Sensible | 5217.44 | 0.14802 | 0.14802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ11 | 1 | DXGF EL1 | Cooling | Sensible | 9489.56 | 0.55446 | 0.55446 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL1 | Heating | Sensible | 7898.8 | 0.21968 | 0.21968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL2 | Cooling | Sensible | 9947.67 | 0.61253 | 0.61253 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL2 | Heating | Sensible | 7893.59 | 0.21954 | 0.21954 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL1 | Cooling | Sensible | 8404.91 | 0.48411 | 0.48411 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL1 | Heating | Sensible | 6372.52 | 0.17567 | 0.17567 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ12 | 3 | DXGF EL2 | Cooling | Sensible | 8115.46 | 0.47569 | 0.47569 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL2 | Heating | Sensible | 6377.57 | 0.17581 | 0.17581 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ13 | 1 | DXGF EL1 | Cooling | Sensible | 8884.13 | 0.51893 | 0.51893 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL1 | Heating | Sensible | 6129.53 | 0.17081 | 0.17081 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ13 | 3 | DXGF EL2 | Cooling | Sensible | 9350.58 | 0.57174 | 0.57174 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL2 | Heating | Sensible | 6122.71 | 0.17062 | 0.17062 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 1 | DXGF EL1 | Cooling | Sensible | 8511.58 | 0.47812 | 0.47812 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL1 | Heating | Sensible | 7537.4 | 0.24293 | 0.24293 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 3 | DXGF EL2 | Cooling | Sensible | 8579.52 | 0.48194 | 0.48194 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL2 | Heating | Sensible | 7532.51 | 0.24277 | 0.24277 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ15 | 1 | DXGF EL1 | Cooling | Sensible | 10860.35 | 0.61866 | 0.61866 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL1 | Heating | Sensible | 6496.97 | 0.18523 | 0.18523 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL2 | Cooling | Sensible | 11216.29 | 0.66796 | 0.66796 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL2 | Heating | Sensible | 6494.09 | 0.18515 | 0.18515 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL1 | Cooling | Sensible | 8239.72 | 0.55403 | 0.55403 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL1 | Heating | Sensible | 6835.19 | 0.18489 | 0.18489 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL2 | Cooling | Sensible | 8991.75 | 0.63248 | 0.63248 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL2 | Heating | Sensible | 6828.3 | 0.1847 | 0.1847 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 2943.2 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 3690.2 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6923.6 | 2.78 | 9.49 | 10.06 | 9.52 | 9.69
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6958.5 | 2.77 | 9.46 | 10.03 | 9.49 | 9.65
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 7030.8 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6884.7 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 6665 | 2.77 | 9.46 | 10.03 | 9.49 | 9.65
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7008.3 | 2.76 | 9.43 | 10 | 9.46 | 9.6
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 7049.7 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7101.5 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 5971.7 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 6619.1 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 7135 | 2.73 | 9.3 | 9.86 | 9.33 | 9.41
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 7802.6 | 2.71 | 9.26 | 9.82 | 9.29 | 9.35
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 7096.1 | 2.75 | 9.38 | 9.95 | 9.41 | 9.53
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 8019.3 | 2.76 | 9.42 | 9.99 | 9.45 | 9.59
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9361.5 | 2.73 | 9.31 | 9.87 | 9.34 | 9.43
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10186.8 | 2.75 | 9.38 | 9.95 | 9.41 | 9.53
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 8137.5 | 2.82 | 9.61 | 10.2 | 9.64 | 9.89
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 8070.2 | 2.81 | 9.58 | 10.16 | 9.61 | 9.84
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10896 | 2.81 | 9.58 | 10.16 | 9.61 | 9.84
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 11272 | 2.78 | 9.48 | 10.06 | 9.52 | 9.69
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9409.9 | 2.8 | 9.56 | 10.14 | 9.6 | 9.81
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 8858.6 | 2.78 | 9.5 | 10.08 | 9.53 | 9.72
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10178.4 | 2.81 | 9.57 | 10.16 | 9.61 | 9.83
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10599.6 | 2.78 | 9.49 | 10.07 | 9.53 | 9.71
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 10097.6 | 2.84 | 9.67 | 10.27 | 9.71 | 9.99
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 9864.7 | 2.82 | 9.63 | 10.22 | 9.67 | 9.93
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 13059.7 | 2.83 | 9.67 | 10.27 | 9.71 | 9.99
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 13401 | 2.81 | 9.61 | 10.19 | 9.64 | 9.88
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL1 COOLING COIL | 9742 | 2.76 | 9.42 | 9.99 | 9.45 | 9.59
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 10428 | 2.73 | 9.32 | 9.88 | 9.35 | 9.44
SWHC031-03 Furnace_DMo | DMo&0&rNCGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXGF EL1 | Heating | Sensible | 3751.47 | 0.0874 | 0.0874 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ01 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 4 | DXGF EL2 | Heating | Sensible | 3746.03 | 0.0872 | 0.0872 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ02 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 2 | DXGF EL1 | Heating | Sensible | 5400.93 | 0.13973 | 0.13973 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ02 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 4 | DXGF EL2 | Heating | Sensible | 5385.24 | 0.13933 | 0.13933 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ03 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 2 | DXGF EL1 | Heating | Sensible | 4334.93 | 0.11346 | 0.11346 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ03 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 4 | DXGF EL2 | Heating | Sensible | 4329.87 | 0.11333 | 0.11333 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 2 | DXGF EL1 | Heating | Sensible | 4598.25 | 0.12019 | 0.12019 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ04 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 4 | DXGF EL2 | Heating | Sensible | 4592.43 | 0.12004 | 0.12004 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ05 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 2 | DXGF EL1 | Heating | Sensible | 5152.73 | 0.1356 | 0.1356 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ05 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 4 | DXGF EL2 | Heating | Sensible | 5147.5 | 0.13546 | 0.13546 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:20
CZ06 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 2 | DXGF EL1 | Heating | Sensible | 2697.81 | 0.0677 | 0.0677 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ06 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 4 | DXGF EL2 | Heating | Sensible | 2692.95 | 0.0676 | 0.0676 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 2 | DXGF EL1 | Heating | Sensible | 2294.96 | 0.0551 | 0.0551 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ07 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 4 | DXGF EL2 | Heating | Sensible | 2289.88 | 0.055 | 0.055 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 2 | DXGF EL1 | Heating | Sensible | 2654.94 | 0.0638 | 0.0638 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ08 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 4 | DXGF EL2 | Heating | Sensible | 2649.77 | 0.0637 | 0.0637 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ09 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 2 | DXGF EL1 | Heating | Sensible | 5759.41 | 0.15909 | 0.15909 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ09 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 4 | DXGF EL2 | Heating | Sensible | 5755.75 | 0.15899 | 0.15899 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ10 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 2 | DXGF EL1 | Heating | Sensible | 5223.16 | 0.14818 | 0.14818 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ10 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 4 | DXGF EL2 | Heating | Sensible | 5217.44 | 0.14802 | 0.14802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ11 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 2 | DXGF EL1 | Heating | Sensible | 7898.8 | 0.21968 | 0.21968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 4 | DXGF EL2 | Heating | Sensible | 7893.59 | 0.21954 | 0.21954 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 2 | DXGF EL1 | Heating | Sensible | 6372.52 | 0.17567 | 0.17567 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ12 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 4 | DXGF EL2 | Heating | Sensible | 6377.57 | 0.17581 | 0.17581 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 05:20
CZ13 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 2 | DXGF EL1 | Heating | Sensible | 6129.53 | 0.17081 | 0.17081 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ13 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 4 | DXGF EL2 | Heating | Sensible | 6122.71 | 0.17062 | 0.17062 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 2 | DXGF EL1 | Heating | Sensible | 7537.4 | 0.24293 | 0.24293 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ14 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 4 | DXGF EL2 | Heating | Sensible | 7532.51 | 0.24277 | 0.24277 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 05:10
CZ15 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 2 | DXGF EL1 | Heating | Sensible | 6496.97 | 0.18523 | 0.18523 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 4 | DXGF EL2 | Heating | Sensible | 6494.09 | 0.18515 | 0.18515 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 2 | DXGF EL1 | Heating | Sensible | 6835.19 | 0.18489 | 0.18489 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL2 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 4 | DXGF EL2 | Heating | Sensible | 6828.3 | 0.1847 | 0.1847 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
SWHC031-03 Furnace_MFm_Ex | MFm&0&rNCGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1864.88 | 0.0448 | 0.0448 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3169.2 | 0.0762 | 0.0762 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1211.38 | 0.0291 | 0.0291 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ01 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2327.82 | 0.056 | 0.056 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ01 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1923.51 | 0.0462 | 0.0462 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3252.56 | 0.0782 | 0.0782 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1875.28 | 0.0451 | 0.0451 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3177.36 | 0.0764 | 0.0764 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1221.57 | 0.0294 | 0.0294 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ01 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2336.02 | 0.0562 | 0.0562 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ01 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1933.83 | 0.0465 | 0.0465 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3258.29 | 0.0783 | 0.0783 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1873.91 | 0.0451 | 0.0451 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3175.93 | 0.0764 | 0.0764 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1211.39 | 0.0291 | 0.0291 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ01 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2327.8 | 0.056 | 0.056 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ01 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1913.87 | 0.046 | 0.046 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3242.98 | 0.078 | 0.078 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1924.23 | 0.0463 | 0.0463 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3253.08 | 0.0782 | 0.0782 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1221.58 | 0.0294 | 0.0294 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ01 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2336.11 | 0.0562 | 0.0562 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ01 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1884.32 | 0.0453 | 0.0453 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ01 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3184.09 | 0.0766 | 0.0766 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ02 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3368.08 | 0.0926 | 0.0926 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5208.91 | 0.14338 | 0.14338 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 2429.81 | 0.0669 | 0.0669 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 4083.48 | 0.11234 | 0.11234 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3407.67 | 0.0938 | 0.0938 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5213.6 | 0.14343 | 0.14343 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3368.07 | 0.0926 | 0.0926 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5208.9 | 0.14338 | 0.14338 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 2429.81 | 0.0669 | 0.0669 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 4083.4 | 0.11234 | 0.11234 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3407.64 | 0.0938 | 0.0938 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5210.85 | 0.14336 | 0.14336 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3369.56 | 0.0927 | 0.0927 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5211.33 | 0.14345 | 0.14345 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 2443.18 | 0.0672 | 0.0672 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 4098.23 | 0.11275 | 0.11275 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3421.38 | 0.0942 | 0.0942 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5225.73 | 0.14376 | 0.14376 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3407.68 | 0.0938 | 0.0938 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5213.47 | 0.14343 | 0.14343 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 2429.81 | 0.0669 | 0.0669 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 4083.56 | 0.11234 | 0.11234 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3355.65 | 0.0923 | 0.0923 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5196.93 | 0.14305 | 0.14305 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ03 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2497.08 | 0.0681 | 0.0681 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:24
CZ03 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3846.35 | 0.10543 | 0.10543 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1704.22 | 0.0466 | 0.0466 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:36
CZ03 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2856.52 | 0.0781 | 0.0781 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2584.12 | 0.0709 | 0.0709 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3964.57 | 0.10872 | 0.10872 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2504.37 | 0.0683 | 0.0683 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:24
CZ03 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3848.71 | 0.1055 | 0.1055 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1711.2 | 0.0468 | 0.0468 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:36
CZ03 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2858.78 | 0.0782 | 0.0782 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2591.16 | 0.0711 | 0.0711 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3964.65 | 0.10872 | 0.10872 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2504.37 | 0.0683 | 0.0683 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:24
CZ03 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3848.65 | 0.10549 | 0.10549 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1711.2 | 0.0468 | 0.0468 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:36
CZ03 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2858.82 | 0.0782 | 0.0782 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2591.16 | 0.0711 | 0.0711 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3964.83 | 0.10872 | 0.10872 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2584.12 | 0.0709 | 0.0709 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3964.39 | 0.10871 | 0.10871 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1704.22 | 0.0466 | 0.0466 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:36
CZ03 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2856.52 | 0.0781 | 0.0781 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2497.08 | 0.0681 | 0.0681 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:24
CZ03 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ03 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3846.4 | 0.10543 | 0.10543 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ04 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2603.35 | 0.0746 | 0.0746 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4045.16 | 0.1159 | 0.1159 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1765.65 | 0.0506 | 0.0506 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3062.08 | 0.0877 | 0.0877 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ04 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2633.06 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4057.53 | 0.11626 | 0.11626 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2615.52 | 0.0749 | 0.0749 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4057.86 | 0.11627 | 0.11627 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1777.65 | 0.0509 | 0.0509 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3074.88 | 0.0881 | 0.0881 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ04 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2645.15 | 0.0758 | 0.0758 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4068.72 | 0.11658 | 0.11658 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2614.01 | 0.0749 | 0.0749 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4055.89 | 0.11621 | 0.11621 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1765.65 | 0.0506 | 0.0506 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3062.05 | 0.0877 | 0.0877 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ04 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2622.22 | 0.0751 | 0.0751 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4044.6 | 0.11589 | 0.11589 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2634.35 | 0.0755 | 0.0755 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4060.81 | 0.11635 | 0.11635 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ04 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1777.65 | 0.0509 | 0.0509 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3074.97 | 0.0881 | 0.0881 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ04 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2626.18 | 0.0752 | 0.0752 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ04 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4068.59 | 0.11657 | 0.11657 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ05 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3351.77 | 0.0931 | 0.0931 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ05 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4791.05 | 0.13309 | 0.13309 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 2363.91 | 0.0657 | 0.0657 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3590.85 | 0.0997 | 0.0997 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3408.8 | 0.0947 | 0.0947 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4877.34 | 0.13549 | 0.13549 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3365.45 | 0.0935 | 0.0935 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ05 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4801.81 | 0.13339 | 0.13339 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 2377.43 | 0.066 | 0.066 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3601.56 | 0.10005 | 0.10005 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3422.34 | 0.0951 | 0.0951 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4885.67 | 0.13572 | 0.13572 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3363.68 | 0.0934 | 0.0934 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ05 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4799.98 | 0.13334 | 0.13334 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 2363.92 | 0.0657 | 0.0657 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3590.84 | 0.0997 | 0.0997 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3395.93 | 0.0943 | 0.0943 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4865.47 | 0.13516 | 0.13516 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3409.52 | 0.0947 | 0.0947 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4878.32 | 0.13551 | 0.13551 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 2377.44 | 0.066 | 0.066 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3601.65 | 0.10005 | 0.10005 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:18
CZ05 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3377.36 | 0.0938 | 0.0938 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ05 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ05 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4810.72 | 0.13363 | 0.13363 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ06 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1989.71 | 0.0555 | 0.0555 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3162.21 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ06 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1440.53 | 0.0401 | 0.0401 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2389.32 | 0.0666 | 0.0666 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2010.14 | 0.056 | 0.056 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3160.75 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1994.47 | 0.0556 | 0.0556 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3162.93 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ06 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1445.19 | 0.0403 | 0.0403 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2389.94 | 0.0666 | 0.0666 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2014.85 | 0.0562 | 0.0562 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3159.32 | 0.088 | 0.088 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1994.47 | 0.0556 | 0.0556 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3162.87 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ06 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1445.19 | 0.0403 | 0.0403 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2389.97 | 0.0666 | 0.0666 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2014.85 | 0.0562 | 0.0562 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3159.49 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2010.14 | 0.056 | 0.056 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3160.6 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1440.53 | 0.0401 | 0.0401 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2389.32 | 0.0666 | 0.0666 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ06 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1989.71 | 0.0555 | 0.0555 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ06 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ06 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3162.27 | 0.0881 | 0.0881 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ07 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2281.46 | 0.0641 | 0.0641 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3633.82 | 0.10209 | 0.10209 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1723.01 | 0.0484 | 0.0484 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2869.59 | 0.0806 | 0.0806 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2303.25 | 0.0647 | 0.0647 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3630.81 | 0.102 | 0.102 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2270.9 | 0.0638 | 0.0638 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3624.68 | 0.10183 | 0.10183 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1712.88 | 0.0481 | 0.0481 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2860.15 | 0.0804 | 0.0804 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2293.02 | 0.0644 | 0.0644 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3619.11 | 0.10167 | 0.10167 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2271.81 | 0.0638 | 0.0638 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3625.79 | 0.10186 | 0.10186 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1723.01 | 0.0484 | 0.0484 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2869.55 | 0.0806 | 0.0806 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2311.91 | 0.065 | 0.065 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3636.56 | 0.10216 | 0.10216 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2301.71 | 0.0647 | 0.0647 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3629.37 | 0.10196 | 0.10196 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1712.88 | 0.0481 | 0.0481 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2860.22 | 0.0804 | 0.0804 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2261.25 | 0.0635 | 0.0635 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ07 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3616.65 | 0.10161 | 0.10161 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2137.84 | 0.059 | 0.059 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3391.58 | 0.0935 | 0.0935 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1445.92 | 0.0399 | 0.0399 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2522.45 | 0.0696 | 0.0696 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ08 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2147.11 | 0.0592 | 0.0592 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3381.62 | 0.0933 | 0.0933 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2126 | 0.0586 | 0.0586 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3380.53 | 0.0932 | 0.0932 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1434.24 | 0.0396 | 0.0396 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2511.07 | 0.0693 | 0.0693 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ08 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2135.31 | 0.0589 | 0.0589 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3367.94 | 0.0929 | 0.0929 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2127.22 | 0.0587 | 0.0587 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3381.82 | 0.0933 | 0.0933 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1445.92 | 0.0399 | 0.0399 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2522.41 | 0.0696 | 0.0696 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ08 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2157.86 | 0.0595 | 0.0595 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3389.07 | 0.0935 | 0.0935 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2146.09 | 0.0592 | 0.0592 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3379.99 | 0.0932 | 0.0932 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ08 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1434.24 | 0.0396 | 0.0396 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2511.15 | 0.0693 | 0.0693 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ08 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2115.38 | 0.0583 | 0.0583 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ08 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ08 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3370.77 | 0.093 | 0.093 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ09 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2208.52 | 0.0648 | 0.0648 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3494.38 | 0.1026 | 0.1026 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1465.37 | 0.043 | 0.043 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2614.68 | 0.0768 | 0.0768 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:12
CZ09 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2223.39 | 0.0653 | 0.0653 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3494.68 | 0.10261 | 0.10261 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2204.44 | 0.0647 | 0.0647 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3489.2 | 0.10245 | 0.10245 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1461.35 | 0.0429 | 0.0429 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2609.3 | 0.0766 | 0.0766 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:12
CZ09 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2219.3 | 0.0652 | 0.0652 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3486.64 | 0.10237 | 0.10237 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2204.43 | 0.0647 | 0.0647 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3489.13 | 0.10245 | 0.10245 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1461.35 | 0.0429 | 0.0429 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2609.32 | 0.0766 | 0.0766 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:12
CZ09 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2223.02 | 0.0653 | 0.0653 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3491.27 | 0.10251 | 0.10251 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2223.04 | 0.0653 | 0.0653 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3493.65 | 0.10258 | 0.10258 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ09 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1461.35 | 0.0429 | 0.0429 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2609.36 | 0.0766 | 0.0766 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:12
CZ09 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2204.43 | 0.0647 | 0.0647 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:00
CZ09 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ09 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3489.15 | 0.10245 | 0.10245 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ10 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2413.48 | 0.0685 | 0.0685 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3870.98 | 0.10982 | 0.10982 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1601.69 | 0.0454 | 0.0454 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2867.83 | 0.0814 | 0.0814 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ10 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2448.24 | 0.0695 | 0.0695 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3883.11 | 0.11017 | 0.11017 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2426.99 | 0.0689 | 0.0689 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3884.11 | 0.11019 | 0.11019 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1615.02 | 0.0458 | 0.0458 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2881.05 | 0.0817 | 0.0817 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ10 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2461.68 | 0.0698 | 0.0698 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3893.81 | 0.11047 | 0.11047 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2425.53 | 0.0688 | 0.0688 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3882.4 | 0.11015 | 0.11015 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1601.7 | 0.0454 | 0.0454 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2867.8 | 0.0814 | 0.0814 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ10 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2436.01 | 0.0691 | 0.0691 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3869.42 | 0.10978 | 0.10978 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2449.48 | 0.0695 | 0.0695 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3884.74 | 0.11021 | 0.11021 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ10 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1615.03 | 0.0458 | 0.0458 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2881.13 | 0.0817 | 0.0817 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:12
CZ10 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2439.04 | 0.0692 | 0.0692 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:00
CZ10 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ10 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3895.53 | 0.11052 | 0.11052 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 04:06
CZ11 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3002.27 | 0.0821 | 0.0821 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4686.91 | 0.1282 | 0.1282 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 2009.32 | 0.0548 | 0.0548 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3536.72 | 0.0968 | 0.0968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2982.97 | 0.0815 | 0.0815 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4699.55 | 0.1286 | 0.1286 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2997.27 | 0.082 | 0.082 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4688.64 | 0.12824 | 0.12824 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 2004.42 | 0.0547 | 0.0547 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3538.38 | 0.0968 | 0.0968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2978.06 | 0.0813 | 0.0813 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4698.96 | 0.12858 | 0.12858 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2998.07 | 0.082 | 0.082 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4688.48 | 0.12824 | 0.12824 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 2009.32 | 0.0548 | 0.0548 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3536.69 | 0.0968 | 0.0968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2987.2 | 0.0816 | 0.0816 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4696.02 | 0.1285 | 0.1285 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2982.31 | 0.0815 | 0.0815 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4699.5 | 0.1286 | 0.1286 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 2004.42 | 0.0547 | 0.0547 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3538.45 | 0.0968 | 0.0968 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2993.07 | 0.0819 | 0.0819 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ11 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4690.26 | 0.12829 | 0.12829 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2958.27 | 0.0782 | 0.0782 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4308.55 | 0.11613 | 0.11613 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1998.27 | 0.0531 | 0.0531 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3386.74 | 0.0915 | 0.0915 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3042.84 | 0.0813 | 0.0813 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4585.47 | 0.12401 | 0.12401 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2972.11 | 0.0786 | 0.0786 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4319.37 | 0.11642 | 0.11642 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 2012.28 | 0.0534 | 0.0534 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3397.67 | 0.0918 | 0.0918 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3056.93 | 0.0817 | 0.0817 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4595.57 | 0.12428 | 0.12428 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2969.86 | 0.0785 | 0.0785 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4317.55 | 0.11638 | 0.11638 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1998.27 | 0.0531 | 0.0531 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3386.64 | 0.0915 | 0.0915 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3042.82 | 0.0813 | 0.0813 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4582.93 | 0.12394 | 0.12394 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3042.83 | 0.0813 | 0.0813 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4585.19 | 0.124 | 0.124 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1998.27 | 0.0531 | 0.0531 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3386.68 | 0.0915 | 0.0915 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2969.86 | 0.0785 | 0.0785 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ12 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4317.53 | 0.11637 | 0.11637 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ13 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3734.7 | 0.10408 | 0.10408 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5305.09 | 0.14784 | 0.14784 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 2735.2 | 0.0761 | 0.0761 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ13 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 4027.9 | 0.11225 | 0.11225 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3735.36 | 0.10393 | 0.10393 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5267.07 | 0.14678 | 0.14678 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3751.9 | 0.10456 | 0.10456 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5321.76 | 0.1483 | 0.1483 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 2751.42 | 0.0765 | 0.0765 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ13 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 4044.8 | 0.11272 | 0.11272 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3750.96 | 0.10436 | 0.10436 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5281.19 | 0.14717 | 0.14717 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3751.91 | 0.10456 | 0.10456 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5321.7 | 0.1483 | 0.1483 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 2751.42 | 0.0765 | 0.0765 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ13 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 4044.84 | 0.11272 | 0.11272 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3750.96 | 0.10436 | 0.10436 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5281.4 | 0.14718 | 0.14718 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3735.36 | 0.10393 | 0.10393 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5266.88 | 0.14677 | 0.14677 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 2735.2 | 0.0761 | 0.0761 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:00
CZ13 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 4027.91 | 0.11225 | 0.11225 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3734.7 | 0.10408 | 0.10408 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ13 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5305.15 | 0.14784 | 0.14784 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ14 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3055.93 | 0.0903 | 0.0903 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4840.19 | 0.14291 | 0.14291 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1972.75 | 0.0583 | 0.0583 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3511.78 | 0.1037 | 0.1037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3095.43 | 0.0915 | 0.0915 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4859.4 | 0.14351 | 0.14351 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3052.47 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4846.09 | 0.14308 | 0.14308 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1969.37 | 0.0582 | 0.0582 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3517.58 | 0.10387 | 0.10387 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3091.99 | 0.0914 | 0.0914 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4863.04 | 0.14362 | 0.14362 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3053.06 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4845.58 | 0.14307 | 0.14307 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1972.75 | 0.0583 | 0.0583 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3511.76 | 0.1037 | 0.1037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3098.32 | 0.0915 | 0.0915 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4852.08 | 0.1433 | 0.1433 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3094.91 | 0.0914 | 0.0914 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4859.63 | 0.14352 | 0.14352 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1969.37 | 0.0582 | 0.0582 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3517.65 | 0.10387 | 0.10387 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ14 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3049.6 | 0.0901 | 0.0901 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4851.48 | 0.14324 | 0.14324 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ15 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2701.26 | 0.0757 | 0.0757 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4063.3 | 0.11387 | 0.11387 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1827.87 | 0.0512 | 0.0512 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2985.88 | 0.0837 | 0.0837 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2717.82 | 0.0762 | 0.0762 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4054.29 | 0.11362 | 0.11362 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2696.61 | 0.0756 | 0.0756 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4064.96 | 0.11391 | 0.11391 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1823.27 | 0.0511 | 0.0511 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2987.45 | 0.0837 | 0.0837 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2713.19 | 0.076 | 0.076 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4053.82 | 0.1136 | 0.1136 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2696.61 | 0.0756 | 0.0756 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4064.92 | 0.11391 | 0.11391 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1823.28 | 0.0511 | 0.0511 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2987.49 | 0.0837 | 0.0837 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2717.22 | 0.0761 | 0.0761 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4052.47 | 0.11356 | 0.11356 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2717.23 | 0.0761 | 0.0761 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4054.23 | 0.11361 | 0.11361 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1823.28 | 0.0511 | 0.0511 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2987.52 | 0.0837 | 0.0837 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2696.61 | 0.0756 | 0.0756 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ15 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4064.97 | 0.11391 | 0.11391 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ16 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3927.81 | 0.11525 | 0.11525 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5642.61 | 0.16556 | 0.16556 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 2565.34 | 0.0753 | 0.0753 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 4132.77 | 0.12126 | 0.12126 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3939.02 | 0.11557 | 0.11557 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5649.48 | 0.16576 | 0.16576 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3927.81 | 0.11525 | 0.11525 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5642.66 | 0.16556 | 0.16556 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 2565.33 | 0.0753 | 0.0753 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 4132.71 | 0.12126 | 0.12126 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3939 | 0.11557 | 0.11557 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5647.43 | 0.1657 | 0.1657 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3928.71 | 0.11527 | 0.11527 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5642.24 | 0.16555 | 0.16555 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 2570.77 | 0.0754 | 0.0754 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 4128.1 | 0.12112 | 0.12112 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3944.47 | 0.11573 | 0.11573 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5642.99 | 0.16557 | 0.16557 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3939.02 | 0.11557 | 0.11557 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5649.31 | 0.16576 | 0.16576 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 2565.34 | 0.0753 | 0.0753 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 4132.76 | 0.12126 | 0.12126 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
CZ16 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3923.22 | 0.11511 | 0.11511 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:18
CZ16 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ16 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5646.89 | 0.16568 | 0.16568 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 04:06
SWHC031-03 Furnace_MFm_Ex | MFm&0&rDXGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ01 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1099.1 | 0.0264 | 0.0264 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 1473.72 | 0.0959 | 0.0959 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3041.93 | 0.0731 | 0.0731 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 135.57 | 0.00326 | 0.00326 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 1376.08 | 0.0896 | 0.0896 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2172.84 | 0.0522 | 0.0522 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 902.87 | 0.0217 | 0.0217 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 1095.24 | 0.0713 | 0.0713 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3112.59 | 0.0748 | 0.0748 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1109.59 | 0.0267 | 0.0267 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 4318.65 | 0.28116 | 0.28116 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3050.38 | 0.0733 | 0.0733 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 141.24 | 0.0034 | 0.0034 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 4303.58 | 0.28018 | 0.28018 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2181.46 | 0.0524 | 0.0524 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 908.23 | 0.0218 | 0.0218 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 4309.5 | 0.28056 | 0.28056 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3118.64 | 0.075 | 0.075 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1107.96 | 0.0266 | 0.0266 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 4148.96 | 0.27011 | 0.27011 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3048.89 | 0.0733 | 0.0733 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ01 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 135.58 | 0.00326 | 0.00326 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 398.22 | 0.0259 | 0.0259 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2172.82 | 0.0522 | 0.0522 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 893.4 | 0.0215 | 0.0215 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 2275.33 | 0.14813 | 0.14813 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3102.56 | 0.0746 | 0.0746 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 898.79 | 0.0216 | 0.0216 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 2301.52 | 0.14984 | 0.14984 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3112.96 | 0.0748 | 0.0748 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:36
CZ01 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 141.25 | 0.0034 | 0.0034 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ01 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 384.73 | 0.025 | 0.025 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2181.54 | 0.0525 | 0.0525 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 15:06
CZ01 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 0 | 0 | 0 |  | 0:00
CZ01 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1118.45 | 0.0269 | 0.0269 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 45648
CZ01 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 4145.71 | 0.2699 | 0.2699 | CA_EUREKA ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ01 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3057.34 | 0.0735 | 0.0735 | CA_EUREKA ANN HTG 99.6% CONDNS DB | 2024-12-21 17:30
CZ02 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1086.35 | 0.0623 | 0.0623 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 236.6 | 0.00653 | 0.00653 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4354.14 | 0.25238 | 0.25238 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4674 | 0.12877 | 0.12877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 879.28 | 0.0515 | 0.0515 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3725.8 | 0.21815 | 0.21815 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3443.86 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1131.11 | 0.0652 | 0.0652 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 609.11 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4403.69 | 0.25399 | 0.25399 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4642.6 | 0.12774 | 0.12774 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1071.46 | 0.0615 | 0.0615 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 236.6 | 0.00653 | 0.00653 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7110.44 | 0.41722 | 0.41722 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4673.99 | 0.12877 | 0.12877 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 862.9 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6631.78 | 0.38914 | 0.38914 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3443.77 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1115.98 | 0.0643 | 0.0643 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 609.1 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7117.92 | 0.41766 | 0.41766 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4639.92 | 0.12767 | 0.12767 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1070.32 | 0.0614 | 0.0614 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 231.05 | 0.00638 | 0.00638 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7110.83 | 0.41706 | 0.41706 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4676.62 | 0.12884 | 0.12884 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 861.8 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3528.63 | 0.2066 | 0.2066 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3459.76 | 0.0953 | 0.0953 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1123.95 | 0.0647 | 0.0647 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 615.44 | 0.017 | 0.017 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4331.08 | 0.24973 | 0.24973 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4655.41 | 0.12809 | 0.12809 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1125.09 | 0.0648 | 0.0648 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 609.14 | 0.0168 | 0.0168 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 22:00
CZ02 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4340.86 | 0.25029 | 0.25029 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4642.59 | 0.12774 | 0.12774 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ02 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 862.86 | 0.0505 | 0.0505 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ02 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3534.62 | 0.20695 | 0.20695 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3443.95 | 0.0949 | 0.0949 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:12
CZ02 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1071.04 | 0.0614 | 0.0614 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 213.61 | 0.0059 | 0.0059 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 23:00
CZ02 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7128.45 | 0.41809 | 0.41809 | CA_NAPA-CO ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ02 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4661.27 | 0.12842 | 0.12842 | CA_NAPA-CO ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ03 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 989.76 | 0.069 | 0.069 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2087.07 | 0.057 | 0.057 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3953.05 | 0.27559 | 0.27559 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3812.15 | 0.10449 | 0.10449 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 689.11 | 0.048 | 0.048 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1316.48 | 0.036 | 0.036 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3390.81 | 0.23639 | 0.23639 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2814.11 | 0.0772 | 0.0772 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1008.25 | 0.0703 | 0.0703 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2208.84 | 0.0607 | 0.0607 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3650.84 | 0.25452 | 0.25452 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3925.96 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 978.03 | 0.0682 | 0.0682 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2094.25 | 0.0572 | 0.0572 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 6721.41 | 0.46858 | 0.46858 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3814.53 | 0.10456 | 0.10456 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 678.26 | 0.0473 | 0.0473 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1323.29 | 0.0362 | 0.0362 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6321.6 | 0.4407 | 0.4407 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2816.45 | 0.0773 | 0.0773 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 996.71 | 0.0695 | 0.0695 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2215.8 | 0.0608 | 0.0608 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 6724.7 | 0.46881 | 0.46881 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3926.08 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 978.43 | 0.0682 | 0.0682 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2094.25 | 0.0572 | 0.0572 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6588.19 | 0.45929 | 0.45929 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3814.48 | 0.10456 | 0.10456 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 681.81 | 0.0475 | 0.0475 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1323.29 | 0.0362 | 0.0362 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2694.1 | 0.18782 | 0.18782 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2816.49 | 0.0773 | 0.0773 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1010.39 | 0.0704 | 0.0704 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2215.8 | 0.0608 | 0.0608 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4808.75 | 0.33525 | 0.33525 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3926.26 | 0.10795 | 0.10795 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1006.08 | 0.0701 | 0.0701 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2208.84 | 0.0607 | 0.0607 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4804.58 | 0.33495 | 0.33495 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3925.78 | 0.10794 | 0.10794 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 677.96 | 0.0473 | 0.0473 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1316.48 | 0.036 | 0.036 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 07:06
CZ03 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2686.44 | 0.18728 | 0.18728 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2814.11 | 0.0772 | 0.0772 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ03 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 974.3 | 0.0679 | 0.0679 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2087.07 | 0.057 | 0.057 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ03 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6595.78 | 0.45982 | 0.45982 | CA_OAKLAND-METRO-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ03 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3812.2 | 0.1045 | 0.1045 | CA_OAKLAND-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 17:42
CZ04 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1208.79 | 0.0693 | 0.0693 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 235.9 | 0.00676 | 0.00676 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4531.08 | 0.25999 | 0.25999 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3684.55 | 0.10557 | 0.10557 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 975.81 | 0.0571 | 0.0571 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3864.33 | 0.2262 | 0.2262 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2617.1 | 0.075 | 0.075 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1251.14 | 0.0721 | 0.0721 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 472.56 | 0.0135 | 0.0135 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4572.1 | 0.26364 | 0.26364 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3676.69 | 0.10535 | 0.10535 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1197.67 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 251.75 | 0.00722 | 0.00722 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7270.74 | 0.42653 | 0.42653 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3698.42 | 0.10597 | 0.10597 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 964.41 | 0.0565 | 0.0565 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6755.96 | 0.39633 | 0.39633 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2630.99 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1240.69 | 0.0714 | 0.0714 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 479.07 | 0.0137 | 0.0137 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7268.42 | 0.42639 | 0.42639 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3687.9 | 0.10567 | 0.10567 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1197.43 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 258.07 | 0.0074 | 0.0074 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7278.03 | 0.42676 | 0.42676 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3696.66 | 0.10592 | 0.10592 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 963.89 | 0.0564 | 0.0564 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3728.62 | 0.21826 | 0.21826 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2617.12 | 0.075 | 0.075 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1246.77 | 0.0718 | 0.0718 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 461.89 | 0.0132 | 0.0132 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4535.27 | 0.26145 | 0.26145 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3663.54 | 0.10497 | 0.10497 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1246.85 | 0.0718 | 0.0718 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 468.42 | 0.0134 | 0.0134 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 22:00
CZ04 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4536.45 | 0.26151 | 0.26151 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3679.22 | 0.10542 | 0.10542 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ04 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 963.68 | 0.0564 | 0.0564 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ04 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3728.96 | 0.21828 | 0.21828 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2631.13 | 0.0754 | 0.0754 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:18
CZ04 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1196.9 | 0.0687 | 0.0687 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 274.09 | 0.00785 | 0.00785 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 00:06
CZ04 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7292.01 | 0.42758 | 0.42758 | CA_SAN-JOSE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ04 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3710.51 | 0.10631 | 0.10631 | CA_SAN-JOSE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:12
CZ05 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 707.96 | 0.0474 | 0.0474 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2575.92 | 0.0716 | 0.0716 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3801.71 | 0.25469 | 0.25469 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4738.24 | 0.13162 | 0.13162 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 523.38 | 0.0351 | 0.0351 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1608.95 | 0.0447 | 0.0447 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3106.07 | 0.20809 | 0.20809 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3525.27 | 0.0979 | 0.0979 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 751.71 | 0.0504 | 0.0504 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2663.48 | 0.074 | 0.074 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3779.26 | 0.25319 | 0.25319 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4810.85 | 0.13364 | 0.13364 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 690.9 | 0.0463 | 0.0463 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2589.25 | 0.0719 | 0.0719 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7141.09 | 0.47842 | 0.47842 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4748.88 | 0.13192 | 0.13192 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 507.86 | 0.034 | 0.034 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1621.84 | 0.0451 | 0.0451 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6786.57 | 0.45467 | 0.45467 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3536.34 | 0.0982 | 0.0982 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 734.74 | 0.0492 | 0.0492 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2676.6 | 0.0744 | 0.0744 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7130 | 0.47768 | 0.47768 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4819.24 | 0.13388 | 0.13388 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 690.09 | 0.0462 | 0.0462 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2587.6 | 0.0719 | 0.0719 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6949.77 | 0.4656 | 0.4656 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4746.61 | 0.13185 | 0.13185 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 507.96 | 0.034 | 0.034 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1608.96 | 0.0447 | 0.0447 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2819.86 | 0.18892 | 0.18892 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3525.24 | 0.0979 | 0.0979 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 750.03 | 0.0502 | 0.0502 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2651.08 | 0.0736 | 0.0736 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4435.71 | 0.29716 | 0.29716 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4798.91 | 0.13331 | 0.13331 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 748.27 | 0.0501 | 0.0501 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2664.22 | 0.074 | 0.074 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4456.27 | 0.29854 | 0.29854 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4811.81 | 0.13367 | 0.13367 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 506.45 | 0.0339 | 0.0339 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1621.84 | 0.0451 | 0.0451 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2815.55 | 0.18863 | 0.18863 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3536.43 | 0.0982 | 0.0982 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ05 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 688.32 | 0.0461 | 0.0461 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2600.93 | 0.0723 | 0.0723 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 05:00
CZ05 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6971.6 | 0.46706 | 0.46706 | CA_SANTA-MARIA-PUBLIC-AP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ05 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4756.8 | 0.13214 | 0.13214 | CA_SANTA-MARIA-PUBLIC-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ06 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1140.07 | 0.0733 | 0.0733 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1579.43 | 0.044 | 0.044 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4190.29 | 0.2695 | 0.2695 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3104.84 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 789.8 | 0.0508 | 0.0508 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1005.46 | 0.028 | 0.028 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3637.27 | 0.23393 | 0.23393 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2324.94 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1166.78 | 0.075 | 0.075 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1596.84 | 0.0445 | 0.0445 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3915.88 | 0.25185 | 0.25185 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3100.71 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1131.13 | 0.0727 | 0.0727 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1584.05 | 0.0441 | 0.0441 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 6880.25 | 0.44251 | 0.44251 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3105.58 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 781.41 | 0.0503 | 0.0503 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1010.14 | 0.0282 | 0.0282 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6454.17 | 0.41511 | 0.41511 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2325.61 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1157.86 | 0.0745 | 0.0745 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1601.53 | 0.0446 | 0.0446 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 6892.49 | 0.4433 | 0.4433 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3099.32 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1130.97 | 0.0727 | 0.0727 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1584.05 | 0.0441 | 0.0441 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 6745.51 | 0.43384 | 0.43384 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3105.52 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 781.08 | 0.0502 | 0.0502 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1010.14 | 0.0282 | 0.0282 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 2899.41 | 0.18648 | 0.18648 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2325.64 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1162.77 | 0.0748 | 0.0748 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1601.53 | 0.0446 | 0.0446 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5048.39 | 0.32469 | 0.32469 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3099.49 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1166.08 | 0.075 | 0.075 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1596.84 | 0.0445 | 0.0445 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5082.25 | 0.32687 | 0.32687 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3100.55 | 0.0864 | 0.0864 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 784.14 | 0.0504 | 0.0504 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1005.46 | 0.028 | 0.028 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 2909.63 | 0.18714 | 0.18714 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2324.94 | 0.0648 | 0.0648 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ06 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1134.25 | 0.073 | 0.073 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1579.42 | 0.044 | 0.044 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 45648
CZ06 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 6771.29 | 0.4355 | 0.4355 | CA_LOS-ANGELES-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ06 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3104.9 | 0.0865 | 0.0865 | CA_LOS-ANGELES-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 854.64 | 0.0521 | 0.0521 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1838.53 | 0.0517 | 0.0517 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 3928.28 | 0.23023 | 0.23023 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3584.36 | 0.1007 | 0.1007 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 793.25 | 0.0484 | 0.0484 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1256.85 | 0.0353 | 0.0353 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3503.71 | 0.21311 | 0.21311 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2811.52 | 0.079 | 0.079 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 919.84 | 0.0533 | 0.0533 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1858.87 | 0.0522 | 0.0522 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 3868.28 | 0.22527 | 0.22527 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3577.52 | 0.10051 | 0.10051 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 849.68 | 0.0518 | 0.0518 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1828.63 | 0.0514 | 0.0514 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7274.8 | 0.43506 | 0.43506 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3575.13 | 0.10044 | 0.10044 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 787.03 | 0.048 | 0.048 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1246.84 | 0.035 | 0.035 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 6918.14 | 0.4147 | 0.4147 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2801.94 | 0.0787 | 0.0787 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 910.01 | 0.0528 | 0.0528 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1848.4 | 0.0519 | 0.0519 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7281.97 | 0.4357 | 0.4357 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3565.72 | 0.10017 | 0.10017 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 849.24 | 0.0518 | 0.0518 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1829.7 | 0.0514 | 0.0514 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7073.66 | 0.42435 | 0.42435 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3576.27 | 0.10047 | 0.10047 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 786.32 | 0.0479 | 0.0479 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1256.84 | 0.0353 | 0.0353 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3283.54 | 0.19721 | 0.19721 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2811.48 | 0.079 | 0.079 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 921.44 | 0.0534 | 0.0534 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1869.33 | 0.0525 | 0.0525 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4920.36 | 0.29956 | 0.29956 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3583.3 | 0.10067 | 0.10067 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 918.97 | 0.0532 | 0.0532 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1858.88 | 0.0522 | 0.0522 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4982.93 | 0.30388 | 0.30388 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3575.99 | 0.10046 | 0.10046 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 785.21 | 0.0479 | 0.0479 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1246.84 | 0.035 | 0.035 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3294.38 | 0.19787 | 0.19787 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2802.02 | 0.0787 | 0.0787 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 848.17 | 0.0517 | 0.0517 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1819.8 | 0.0511 | 0.0511 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ07 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7106.84 | 0.42739 | 0.42739 | CA_SAN-DIEGO-LINDBERGH-F ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ07 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3567.04 | 0.10021 | 0.10021 | CA_SAN-DIEGO-LINDBERGH-F ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1361.99 | 0.0768 | 0.0768 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1658.92 | 0.0458 | 0.0458 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4861.67 | 0.27861 | 0.27861 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3325.81 | 0.0917 | 0.0917 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1091.07 | 0.0664 | 0.0664 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 960.95 | 0.0265 | 0.0265 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4101.98 | 0.24115 | 0.24115 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2444.9 | 0.0674 | 0.0674 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1462.88 | 0.0841 | 0.0841 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1679.26 | 0.0463 | 0.0463 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4926.55 | 0.28198 | 0.28198 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3310.11 | 0.0913 | 0.0913 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1354.51 | 0.0766 | 0.0766 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1647.36 | 0.0454 | 0.0454 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 8649.25 | 0.51748 | 0.51748 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3314.64 | 0.0914 | 0.0914 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1085.98 | 0.0662 | 0.0662 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 949.47 | 0.0262 | 0.0262 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8069.44 | 0.48503 | 0.48503 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2433.32 | 0.0671 | 0.0671 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1456.28 | 0.0837 | 0.0837 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1667.64 | 0.046 | 0.046 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 8659.78 | 0.52043 | 0.52043 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3296.29 | 0.0909 | 0.0909 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1353.19 | 0.0764 | 0.0764 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1648.46 | 0.0455 | 0.0455 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 8444.71 | 0.5044 | 0.5044 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3315.95 | 0.0915 | 0.0915 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1084.41 | 0.0661 | 0.0661 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 960.95 | 0.0265 | 0.0265 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4017.14 | 0.23616 | 0.23616 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2444.85 | 0.0674 | 0.0674 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1462.46 | 0.0841 | 0.0841 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1689.94 | 0.0466 | 0.0466 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5561.88 | 0.33402 | 0.33402 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3317.58 | 0.0915 | 0.0915 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1461.91 | 0.084 | 0.084 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1678.36 | 0.0463 | 0.0463 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5615.93 | 0.33733 | 0.33733 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3308.35 | 0.0913 | 0.0913 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1084.3 | 0.0661 | 0.0661 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 949.47 | 0.0262 | 0.0262 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4018.65 | 0.24142 | 0.24142 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2433.4 | 0.0671 | 0.0671 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ08 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1352.18 | 0.0764 | 0.0764 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1636.91 | 0.0452 | 0.0452 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 45648
CZ08 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 8467.53 | 0.50947 | 0.50947 | CA_LONG-BEACH-DAUGHERTY- ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ08 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3304.77 | 0.0912 | 0.0912 | CA_LONG-BEACH-DAUGHERTY- ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ09 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1501.7 | 0.0844 | 0.0844 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1794.2 | 0.0527 | 0.0527 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5608.08 | 0.32143 | 0.32143 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3442.09 | 0.10107 | 0.10107 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1144.97 | 0.0674 | 0.0674 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1064.86 | 0.0313 | 0.0313 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4749.6 | 0.27826 | 0.27826 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2551.98 | 0.0749 | 0.0749 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1574.08 | 0.0892 | 0.0892 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1829.27 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5659.97 | 0.32445 | 0.32445 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3436.6 | 0.1009 | 0.1009 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1497.33 | 0.0842 | 0.0842 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9578.91 | 0.56467 | 0.56467 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3436.88 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1139.28 | 0.0671 | 0.0671 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8930.06 | 0.52642 | 0.52642 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2546.55 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1569.16 | 0.0889 | 0.0889 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1825.32 | 0.0536 | 0.0536 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9582.38 | 0.56488 | 0.56488 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3428.53 | 0.10067 | 0.10067 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1495.44 | 0.084 | 0.084 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9460.95 | 0.55755 | 0.55755 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3436.8 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ09 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1138.34 | 0.067 | 0.067 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4668.74 | 0.27439 | 0.27439 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2546.56 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1572.58 | 0.0891 | 0.0891 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1829 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6606.44 | 0.38921 | 0.38921 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3433.16 | 0.1008 | 0.1008 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1572.73 | 0.0891 | 0.0891 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1829.02 | 0.0537 | 0.0537 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6671.38 | 0.39304 | 0.39304 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3435.54 | 0.10087 | 0.10087 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1138.47 | 0.0671 | 0.0671 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1060.99 | 0.0312 | 0.0312 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4670.2 | 0.27448 | 0.27448 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2546.61 | 0.0748 | 0.0748 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1495.49 | 0.0841 | 0.0841 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1790.2 | 0.0526 | 0.0526 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ09 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9481.42 | 0.55876 | 0.55876 | CA_LOS-ANGELES-DOWNTOWN-USC ANN CLG 0.4% CONDNS DB=>MCWB | 2024-08-21
CZ09 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3436.83 | 0.10091 | 0.10091 | CA_LOS-ANGELES-DOWNTOWN-USC ANN HTG 99.6% CONDNS DB | 2024-01-21 04:30
CZ10 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1935.26 | 0.10801 | 0.10801 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1835.28 | 0.0521 | 0.0521 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5422.33 | 0.3026 | 0.3026 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3791.73 | 0.10757 | 0.10757 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1342.55 | 0.0749 | 0.0749 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1007.79 | 0.0286 | 0.0286 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4220.51 | 0.23554 | 0.23554 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2773.66 | 0.0787 | 0.0787 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1970.15 | 0.10997 | 0.10997 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1879.67 | 0.0533 | 0.0533 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5431.58 | 0.30312 | 0.30312 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3796.69 | 0.10771 | 0.10771 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1926.57 | 0.10753 | 0.10753 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1848.49 | 0.0524 | 0.0524 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 8681.24 | 0.49635 | 0.49635 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3805.04 | 0.10795 | 0.10795 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1333.47 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1020.89 | 0.029 | 0.029 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 7940.66 | 0.45502 | 0.45502 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2787.13 | 0.0791 | 0.0791 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1961.52 | 0.10949 | 0.10949 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1892.89 | 0.0537 | 0.0537 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 8707.38 | 0.49805 | 0.49805 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3807.57 | 0.10802 | 0.10802 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1924.92 | 0.10743 | 0.10743 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1847.15 | 0.0524 | 0.0524 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 8512.05 | 0.48375 | 0.48375 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3803.3 | 0.1079 | 0.1079 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1331.99 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1007.79 | 0.0286 | 0.0286 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4013.15 | 0.22397 | 0.22397 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2773.64 | 0.0787 | 0.0787 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1965.5 | 0.10971 | 0.10971 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1867.52 | 0.053 | 0.053 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5368.62 | 0.2996 | 0.2996 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3782.98 | 0.10732 | 0.10732 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1965.72 | 0.10972 | 0.10972 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1880.76 | 0.0534 | 0.0534 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5374.67 | 0.29994 | 0.29994 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3798.48 | 0.10776 | 0.10776 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1332.25 | 0.0744 | 0.0744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1020.9 | 0.029 | 0.029 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4026.23 | 0.22978 | 0.22978 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2787.22 | 0.0791 | 0.0791 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1925.11 | 0.10744 | 0.10744 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1860.37 | 0.0528 | 0.0528 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 45648
CZ10 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 8542.23 | 0.48547 | 0.48547 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3816.61 | 0.10828 | 0.10828 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 2324.58 | 0.13338 | 0.13338 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 774.34 | 0.0212 | 0.0212 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 6458.99 | 0.37501 | 0.37501 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4534.77 | 0.12394 | 0.12394 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1692.96 | 0.1013 | 0.1013 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 5284.41 | 0.31923 | 0.31923 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3310.7 | 0.0904 | 0.0904 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 2389.62 | 0.14133 | 0.14133 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 996.68 | 0.0273 | 0.0273 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 6533.13 | 0.38589 | 0.38589 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4538.03 | 0.12401 | 0.12401 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 2315.78 | 0.13287 | 0.13287 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 771.13 | 0.0211 | 0.0211 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9763.15 | 0.60132 | 0.60132 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4536.25 | 0.12398 | 0.12398 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1684.18 | 0.10222 | 0.10222 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8754.4 | 0.5392 | 0.5392 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3311.97 | 0.0905 | 0.0905 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 2382.24 | 0.14089 | 0.14089 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 994.16 | 0.0272 | 0.0272 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9779.78 | 0.60234 | 0.60234 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4537.35 | 0.12399 | 0.12399 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 2317.85 | 0.13299 | 0.13299 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 770.22 | 0.0211 | 0.0211 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9534.99 | 0.58616 | 0.58616 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4536.2 | 0.12398 | 0.12398 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1686.53 | 0.10092 | 0.10092 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 5218.75 | 0.31756 | 0.31756 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3310.67 | 0.0904 | 0.0904 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 2388.15 | 0.14123 | 0.14123 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1000.82 | 0.0274 | 0.0274 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6528.1 | 0.40101 | 0.40101 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4534.58 | 0.12391 | 0.12391 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 2385.93 | 0.1411 | 0.1411 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 998.31 | 0.0273 | 0.0273 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ11 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6708.14 | 0.41212 | 0.41212 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4537.89 | 0.124 | 0.124 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1684.36 | 0.10079 | 0.10079 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ11 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 5217.1 | 0.31746 | 0.31746 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3312.04 | 0.0905 | 0.0905 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 2315.74 | 0.13287 | 0.13287 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 767.01 | 0.021 | 0.021 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 23:00
CZ11 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9571.33 | 0.58785 | 0.58785 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4537.69 | 0.12402 | 0.12402 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1217.43 | 0.0638 | 0.0638 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2133.43 | 0.0566 | 0.0566 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 4738.9 | 0.2484 | 0.2484 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4380.11 | 0.11835 | 0.11835 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 919.45 | 0.0482 | 0.0482 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1155.63 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 3694.95 | 0.19368 | 0.19368 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3442.08 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1273.03 | 0.0667 | 0.0667 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2238.21 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 4770.61 | 0.25006 | 0.25006 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4618.07 | 0.12484 | 0.12484 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1203.14 | 0.0631 | 0.0631 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2147.85 | 0.057 | 0.057 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 7633.78 | 0.40013 | 0.40013 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4391.06 | 0.11865 | 0.11865 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 905.96 | 0.0475 | 0.0475 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1167.49 | 0.0315 | 0.0315 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 7029.78 | 0.36847 | 0.36847 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3453.68 | 0.0933 | 0.0933 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1258.87 | 0.066 | 0.066 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2251.31 | 0.0604 | 0.0604 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 7704.02 | 0.40382 | 0.40382 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4628.59 | 0.12512 | 0.12512 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1201.58 | 0.063 | 0.063 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2145.41 | 0.0569 | 0.0569 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 7456.78 | 0.39086 | 0.39086 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4388.86 | 0.11859 | 0.11859 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 902.55 | 0.0473 | 0.0473 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1155.6 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 3523.12 | 0.18467 | 0.18467 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3441.96 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1266.43 | 0.0664 | 0.0664 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2238.14 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 4720.68 | 0.24744 | 0.24744 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4615.52 | 0.12477 | 0.12477 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1268.87 | 0.0665 | 0.0665 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2238.16 | 0.0601 | 0.0601 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 4736.3 | 0.24826 | 0.24826 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4617.78 | 0.12483 | 0.12483 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 905.3 | 0.0475 | 0.0475 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1155.6 | 0.0312 | 0.0312 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 3538.11 | 0.18546 | 0.18546 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3442 | 0.093 | 0.093 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ12 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1204.21 | 0.0631 | 0.0631 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2145.4 | 0.0569 | 0.0569 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 07:42
CZ12 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 7573.43 | 0.39697 | 0.39697 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4388.81 | 0.11859 | 0.11859 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ13 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 3160 | 0.1946 | 0.1946 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2821.51 | 0.0786 | 0.0786 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 7493.53 | 0.46111 | 0.46111 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5210.03 | 0.14519 | 0.14519 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 2414.86 | 0.1488 | 0.1488 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1827.55 | 0.0509 | 0.0509 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 6178.75 | 0.38021 | 0.38021 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3913.36 | 0.10906 | 0.10906 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 3187.49 | 0.1963 | 0.1963 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2858.02 | 0.0796 | 0.0796 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 7505.47 | 0.46184 | 0.46184 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5159.42 | 0.14378 | 0.14378 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 3157.76 | 0.19446 | 0.19446 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2838.07 | 0.0791 | 0.0791 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 10452.21 | 0.64375 | 0.64375 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5226.79 | 0.14566 | 0.14566 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 2411.49 | 0.14859 | 0.14859 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1843.99 | 0.0514 | 0.0514 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 9327.16 | 0.5753 | 0.5753 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3930.64 | 0.10954 | 0.10954 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 3186.43 | 0.19623 | 0.19623 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2874.7 | 0.0801 | 0.0801 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 10439.15 | 0.64389 | 0.64389 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5173.82 | 0.14418 | 0.14418 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 3157.16 | 0.19443 | 0.19443 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2838.08 | 0.0791 | 0.0791 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 10594.47 | 0.6531 | 0.6531 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5226.72 | 0.14565 | 0.14565 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 2407.3 | 0.14833 | 0.14833 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1843.99 | 0.0514 | 0.0514 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 6099.82 | 0.37536 | 0.37536 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3930.68 | 0.10954 | 0.10954 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 3181.79 | 0.19595 | 0.19595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2874.7 | 0.0801 | 0.0801 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 7474.48 | 0.45993 | 0.45993 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5174.03 | 0.14419 | 0.14419 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 3186.62 | 0.19624 | 0.19624 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2858.02 | 0.0796 | 0.0796 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 7486.93 | 0.4607 | 0.4607 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5159.23 | 0.14377 | 0.14377 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 2411.21 | 0.14857 | 0.14857 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1827.55 | 0.0509 | 0.0509 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 6108.87 | 0.37591 | 0.37591 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3913.37 | 0.10906 | 0.10906 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ13 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 3160.93 | 0.19466 | 0.19466 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2821.51 | 0.0786 | 0.0786 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 10691.91 | 0.65911 | 0.65911 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5210.08 | 0.14519 | 0.14519 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 01:12
CZ14 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 2550.11 | 0.13839 | 0.13839 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 1255.15 | 0.0371 | 0.0371 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 6043.55 | 0.32798 | 0.32798 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 4640.41 | 0.1371 | 0.1371 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1660.91 | 0.0901 | 0.0901 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4531.32 | 0.24592 | 0.24592 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 3248.15 | 0.096 | 0.096 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 2597.63 | 0.14097 | 0.14097 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 1230.55 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 6074.5 | 0.32966 | 0.32966 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 4621.83 | 0.13655 | 0.13655 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 2549.93 | 0.13838 | 0.13838 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 1252.94 | 0.037 | 0.037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9161.94 | 0.49722 | 0.49722 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 4646.24 | 0.13727 | 0.13727 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1661.63 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8143.58 | 0.44195 | 0.44195 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 3253.72 | 0.0961 | 0.0961 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 2597.98 | 0.14099 | 0.14099 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 1228.86 | 0.0363 | 0.0363 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9256.32 | 0.50234 | 0.50234 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 4625.37 | 0.13666 | 0.13666 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 2549.11 | 0.13834 | 0.13834 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 1252.33 | 0.037 | 0.037 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9098.54 | 0.49378 | 0.49378 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 4645.81 | 0.13726 | 0.13726 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1655.22 | 0.0898 | 0.0898 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4459.04 | 0.24199 | 0.24199 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3248.13 | 0.096 | 0.096 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 2591.4 | 0.14064 | 0.14064 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 1233.36 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 6255.41 | 0.33948 | 0.33948 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 4614.54 | 0.13634 | 0.13634 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 2597.15 | 0.14095 | 0.14095 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 1231.68 | 0.0364 | 0.0364 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 16:00
CZ14 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 6394.27 | 0.34702 | 0.34702 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 4621.95 | 0.13655 | 0.13655 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1661.22 | 0.0902 | 0.0902 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 0 | 0 | 0 |  | 0:00
CZ14 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4472.48 | 0.24272 | 0.24272 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 3253.79 | 0.0961 | 0.0961 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ14 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 2554.89 | 0.13865 | 0.13865 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 1250.13 | 0.0369 | 0.0369 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9225.36 | 0.50066 | 0.50066 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 4651.63 | 0.13743 | 0.13743 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 2024-12-21 08:12
CZ15 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 3231.07 | 0.18011 | 0.18011 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 2112.65 | 0.0592 | 0.0592 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 7725.48 | 0.43652 | 0.43652 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 3985.59 | 0.11169 | 0.11169 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 2294.73 | 0.13738 | 0.13738 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1249.24 | 0.035 | 0.035 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 6237.95 | 0.36318 | 0.36318 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 2899.51 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 3315.63 | 0.18912 | 0.18912 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 2155.46 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 7793.71 | 0.44419 | 0.44419 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 3970.98 | 0.11128 | 0.11128 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 3227.41 | 0.1799 | 0.1799 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 2108.09 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 11297.85 | 0.6793 | 0.6793 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 3987.23 | 0.11174 | 0.11174 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 2291.52 | 0.13719 | 0.13719 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 10045.94 | 0.60553 | 0.60553 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 2901.01 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 3311.78 | 0.1889 | 0.1889 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 2150.9 | 0.0603 | 0.0603 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 11412.33 | 0.69066 | 0.69066 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 3970.47 | 0.11127 | 0.11127 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 3225.6 | 0.17981 | 0.17981 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 2108.08 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 11086.8 | 0.66389 | 0.66389 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 3987.19 | 0.11173 | 0.11173 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 2291.28 | 0.13717 | 0.13717 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 6190.58 | 0.36283 | 0.36283 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 2901.05 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 3315.32 | 0.18909 | 0.18909 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 2154.9 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 7936.76 | 0.47468 | 0.47468 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 3969.12 | 0.11123 | 0.11123 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 3315.67 | 0.18911 | 0.18911 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 2154.92 | 0.0604 | 0.0604 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 8121.34 | 0.49396 | 0.49396 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 3970.87 | 0.11128 | 0.11128 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 2291.57 | 0.13719 | 0.13719 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1244.77 | 0.0349 | 0.0349 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 6243.57 | 0.37944 | 0.37944 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 2901.08 | 0.0813 | 0.0813 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ15 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 3225.81 | 0.17982 | 0.17982 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 2108.08 | 0.0591 | 0.0591 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ15 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 11245.78 | 0.68125 | 0.68125 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 3987.24 | 0.11174 | 0.11174 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 01:12
CZ16 | 1 | DXFG EL1 G_SSE1 | Cooling | Sensible | 1814.63 | 0.11967 | 0.11967 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXFG EL1 G_SSE1 | Heating | Sensible | 3072.15 | 0.0901 | 0.0901 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXFG EL1 T_SSE27 | Cooling | Sensible | 5812.15 | 0.38797 | 0.38797 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXFG EL1 T_SSE27 | Heating | Sensible | 5533.51 | 0.16236 | 0.16236 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 5 | DXFG EL1 G_E3 | Cooling | Sensible | 1290.73 | 0.0877 | 0.0877 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 6 | DXFG EL1 G_E3 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 7 | DXFG EL1 T_E29 | Cooling | Sensible | 4750.24 | 0.32459 | 0.32459 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 8 | DXFG EL1 T_E29 | Heating | Sensible | 4000.07 | 0.11737 | 0.11737 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 9 | DXFG EL1 G_E5 | Cooling | Sensible | 1866.13 | 0.12362 | 0.12362 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 10 | DXFG EL1 G_E5 | Heating | Sensible | 3094.06 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 11 | DXFG EL1 T_E31 | Cooling | Sensible | 5870.5 | 0.39393 | 0.39393 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 12 | DXFG EL1 T_E31 | Heating | Sensible | 5528.31 | 0.16221 | 0.16221 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 13 | DXFG EL1 G_SSW7 | Cooling | Sensible | 1799.01 | 0.11864 | 0.11864 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 14 | DXFG EL1 G_SSW7 | Heating | Sensible | 3072.15 | 0.0901 | 0.0901 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 15 | DXFG EL1 T_SSW33 | Cooling | Sensible | 9533.45 | 0.67542 | 0.67542 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 16 | DXFG EL1 T_SSW33 | Heating | Sensible | 5533.56 | 0.16236 | 0.16236 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 17 | DXFG EL1 G_W9 | Cooling | Sensible | 1275.64 | 0.0869 | 0.0869 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 18 | DXFG EL1 G_W9 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 19 | DXFG EL1 T_W35 | Cooling | Sensible | 8739.6 | 0.61918 | 0.61918 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 20 | DXFG EL1 T_W35 | Heating | Sensible | 4000.01 | 0.11736 | 0.11736 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 21 | DXFG EL1 G_W11 | Cooling | Sensible | 1851.97 | 0.12288 | 0.12288 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 22 | DXFG EL1 G_W11 | Heating | Sensible | 3094.05 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 23 | DXFG EL1 T_W37 | Cooling | Sensible | 9619.84 | 0.68153 | 0.68153 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 24 | DXFG EL1 T_W37 | Heating | Sensible | 5526.26 | 0.16215 | 0.16215 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 25 | DXFG EL2 G_WSW1 | Cooling | Sensible | 1797.79 | 0.11856 | 0.11856 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 26 | DXFG EL2 G_WSW1 | Heating | Sensible | 3072.96 | 0.0902 | 0.0902 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 27 | DXFG EL2 T_WSW27 | Cooling | Sensible | 9295.91 | 0.65636 | 0.65636 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 28 | DXFG EL2 T_WSW27 | Heating | Sensible | 5533.15 | 0.16235 | 0.16235 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 29 | DXFG EL2 G_S3 | Cooling | Sensible | 1274.25 | 0.0868 | 0.0868 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 30 | DXFG EL2 G_S3 | Heating | Sensible | 1691.34 | 0.0496 | 0.0496 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 31 | DXFG EL2 T_S29 | Cooling | Sensible | 4589.08 | 0.31733 | 0.31733 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 32 | DXFG EL2 T_S29 | Heating | Sensible | 3995.49 | 0.11723 | 0.11723 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 33 | DXFG EL2 G_S5 | Cooling | Sensible | 1862.69 | 0.12358 | 0.12358 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 34 | DXFG EL2 G_S5 | Heating | Sensible | 3099.4 | 0.0909 | 0.0909 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 35 | DXFG EL2 T_S31 | Cooling | Sensible | 5810.41 | 0.39288 | 0.39288 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 36 | DXFG EL2 T_S31 | Heating | Sensible | 5521.88 | 0.16202 | 0.16202 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 37 | DXFG EL2 G_N11 | Cooling | Sensible | 1861.04 | 0.12326 | 0.12326 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 38 | DXFG EL2 G_N11 | Heating | Sensible | 3094.07 | 0.0908 | 0.0908 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 39 | DXFG EL2 T_N37 | Cooling | Sensible | 5822.54 | 0.39768 | 0.39768 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 40 | DXFG EL2 T_N37 | Heating | Sensible | 5528.14 | 0.1622 | 0.1622 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 41 | DXFG EL2 G_N9 | Cooling | Sensible | 1272.88 | 0.0867 | 0.0867 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 42 | DXFG EL2 G_N9 | Heating | Sensible | 1686.04 | 0.0495 | 0.0495 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 43 | DXFG EL2 T_N35 | Cooling | Sensible | 4608.96 | 0.32184 | 0.32184 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 44 | DXFG EL2 T_N35 | Heating | Sensible | 4000.07 | 0.11737 | 0.11737 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ16 | 45 | DXFG EL2 G_WNW7 | Cooling | Sensible | 1796.51 | 0.11847 | 0.11847 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 46 | DXFG EL2 G_WNW7 | Heating | Sensible | 3067.6 | 0.09 | 0.09 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 47 | DXFG EL2 T_WNW33 | Cooling | Sensible | 9416.37 | 0.66711 | 0.66711 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 48 | DXFG EL2 T_WNW33 | Heating | Sensible | 5537.74 | 0.16248 | 0.16248 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ01 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 409.4 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 1497.7 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 50.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 1387.8 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 336.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 1210.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 413.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 4355.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 52.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 4340.4 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 338.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 4346.4 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 412.7 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 4379.1 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 50.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 816 | 2.54 | 8.67 | 9.18 | 8.69 | 8.48
CZ01 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 332.8 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 2436.2 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 334.8 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 2470.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 52.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 819.7 | 2.54 | 8.67 | 9.18 | 8.69 | 8.49
CZ01 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 416.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ01 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 4382.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ02 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1120.1 | 2.62 | 8.94 | 9.47 | 8.95 | 8.86
CZ02 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4474.8 | 2.61 | 8.91 | 9.44 | 8.93 | 8.83
CZ02 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 905.8 | 2.61 | 8.9 | 9.42 | 8.91 | 8.81
CZ02 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3826.4 | 2.61 | 8.89 | 9.42 | 8.91 | 8.8
CZ02 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1165.6 | 2.62 | 8.93 | 9.46 | 8.95 | 8.85
CZ02 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 4528.1 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ02 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1104.8 | 2.62 | 8.94 | 9.47 | 8.95 | 8.86
CZ02 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7205 | 2.6 | 8.86 | 9.39 | 8.88 | 8.76
CZ02 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 889 | 2.61 | 8.9 | 9.42 | 8.91 | 8.81
CZ02 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6714.4 | 2.6 | 8.86 | 9.39 | 8.88 | 8.75
CZ02 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1150.1 | 2.62 | 8.93 | 9.46 | 8.95 | 8.85
CZ02 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7211 | 2.6 | 8.86 | 9.39 | 8.88 | 8.76
CZ02 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1103.6 | 2.62 | 8.94 | 9.47 | 8.95 | 8.86
CZ02 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7219.1 | 2.6 | 8.87 | 9.39 | 8.88 | 8.76
CZ02 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 887.8 | 2.61 | 8.9 | 9.42 | 8.91 | 8.81
CZ02 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3624.2 | 2.61 | 8.89 | 9.42 | 8.91 | 8.8
CZ02 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1158.3 | 2.62 | 8.93 | 9.46 | 8.95 | 8.85
CZ02 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4453.7 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ02 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1159.4 | 2.62 | 8.93 | 9.46 | 8.95 | 8.85
CZ02 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4463.7 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ02 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 888.9 | 2.61 | 8.9 | 9.42 | 8.91 | 8.81
CZ02 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3630.4 | 2.61 | 8.89 | 9.42 | 8.91 | 8.8
CZ02 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1104.4 | 2.62 | 8.94 | 9.47 | 8.95 | 8.86
CZ02 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7236.9 | 2.6 | 8.87 | 9.39 | 8.88 | 8.76
CZ03 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1097.1 | 2.55 | 8.71 | 9.22 | 8.72 | 8.53
CZ03 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4269.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 777.3 | 2.56 | 8.74 | 9.26 | 8.76 | 8.58
CZ03 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3662 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1112.5 | 2.55 | 8.7 | 9.21 | 8.71 | 8.52
CZ03 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3942.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1084.9 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ03 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7258.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 765.4 | 2.56 | 8.74 | 9.26 | 8.76 | 8.58
CZ03 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6827.2 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1100.2 | 2.55 | 8.7 | 9.21 | 8.71 | 8.52
CZ03 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7262.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1085.3 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ03 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7115.1 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 769.2 | 2.56 | 8.74 | 9.26 | 8.76 | 8.58
CZ03 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 2909.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1114.4 | 2.55 | 8.7 | 9.21 | 8.71 | 8.52
CZ03 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5193.4 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1109.8 | 2.55 | 8.7 | 9.21 | 8.71 | 8.52
CZ03 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5188.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 765.1 | 2.56 | 8.74 | 9.26 | 8.76 | 8.58
CZ03 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 2901.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ03 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1081 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ03 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7123.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ04 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1256.5 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ04 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4683.2 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ04 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1015.3 | 2.61 | 8.91 | 9.44 | 8.93 | 8.83
CZ04 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3993.1 | 2.61 | 8.9 | 9.43 | 8.92 | 8.81
CZ04 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1299.9 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ04 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 4725.6 | 2.62 | 8.93 | 9.46 | 8.95 | 8.86
CZ04 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1245 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ04 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7426.8 | 2.6 | 8.88 | 9.4 | 8.9 | 8.78
CZ04 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1003.5 | 2.61 | 8.92 | 9.44 | 8.93 | 8.83
CZ04 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6891 | 2.6 | 8.88 | 9.4 | 8.89 | 8.77
CZ04 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1289.2 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ04 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7427.2 | 2.6 | 8.88 | 9.4 | 8.9 | 8.78
CZ04 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1244.8 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ04 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7440.8 | 2.6 | 8.88 | 9.41 | 8.9 | 8.78
CZ04 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1003 | 2.61 | 8.92 | 9.44 | 8.93 | 8.83
CZ04 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3853.4 | 2.61 | 8.9 | 9.43 | 8.92 | 8.82
CZ04 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1295.4 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ04 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4687.7 | 2.62 | 8.93 | 9.46 | 8.95 | 8.86
CZ04 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1295.5 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ04 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4688.9 | 2.62 | 8.93 | 9.46 | 8.95 | 8.86
CZ04 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1002.8 | 2.61 | 8.92 | 9.44 | 8.93 | 8.83
CZ04 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3853.7 | 2.61 | 8.9 | 9.43 | 8.92 | 8.82
CZ04 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1244.2 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ04 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7455 | 2.6 | 8.88 | 9.41 | 8.9 | 8.78
CZ05 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1112.4 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 3945.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 696.5 | 2.54 | 8.67 | 9.18 | 8.68 | 8.48
CZ05 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3223.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1149.5 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3922.3 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1118.4 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7411.4 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 702.2 | 2.54 | 8.67 | 9.18 | 8.68 | 8.48
CZ05 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 7043.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1155.4 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7399.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1117.7 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7212.8 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 696.6 | 2.54 | 8.67 | 9.18 | 8.68 | 8.48
CZ05 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 2926.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1144.2 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4603.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1149.9 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4624.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 702.2 | 2.54 | 8.67 | 9.18 | 8.68 | 8.48
CZ05 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 2922.1 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ05 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1123.5 | 2.54 | 8.66 | 9.17 | 8.68 | 8.47
CZ05 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7235.5 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ06 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1170.2 | 2.55 | 8.71 | 9.23 | 8.73 | 8.54
CZ06 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 4183.1 | 2.54 | 8.66 | 9.17 | 8.67 | 8.47
CZ06 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 811.8 | 2.55 | 8.72 | 9.23 | 8.73 | 8.55
CZ06 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3624 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ06 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1195.5 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ06 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3901.6 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ06 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1161 | 2.55 | 8.71 | 9.23 | 8.73 | 8.54
CZ06 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 6932.5 | 2.54 | 8.68 | 9.19 | 8.69 | 8.49
CZ06 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 803.2 | 2.55 | 8.72 | 9.23 | 8.73 | 8.55
CZ06 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6502 | 2.54 | 8.68 | 9.19 | 8.69 | 8.49
CZ06 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1186.4 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ06 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 6944.2 | 2.54 | 8.68 | 9.19 | 8.69 | 8.49
CZ06 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1160.9 | 2.55 | 8.71 | 9.23 | 8.73 | 8.54
CZ06 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 6807.9 | 2.54 | 8.68 | 9.19 | 8.69 | 8.5
CZ06 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 802.9 | 2.55 | 8.72 | 9.23 | 8.73 | 8.55
CZ06 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 2957.2 | 2.55 | 8.7 | 9.21 | 8.72 | 8.53
CZ06 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1191.4 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ06 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5029.9 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ06 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1194.8 | 2.55 | 8.71 | 9.22 | 8.72 | 8.54
CZ06 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5063.7 | 2.54 | 8.66 | 9.16 | 8.67 | 8.46
CZ06 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 806 | 2.55 | 8.72 | 9.23 | 8.73 | 8.55
CZ06 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 2967.6 | 2.55 | 8.7 | 9.21 | 8.72 | 8.53
CZ06 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1164.2 | 2.55 | 8.71 | 9.23 | 8.73 | 8.54
CZ06 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 6833.8 | 2.54 | 8.68 | 9.19 | 8.69 | 8.5
CZ07 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 985.7 | 2.62 | 8.93 | 9.46 | 8.95 | 8.86
CZ07 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 3961.7 | 2.6 | 8.86 | 9.38 | 8.87 | 8.75
CZ07 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 874.1 | 2.62 | 8.95 | 9.48 | 8.96 | 8.88
CZ07 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 3563.7 | 2.58 | 8.8 | 9.32 | 8.82 | 8.67
CZ07 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1151.9 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ07 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 3949.7 | 2.61 | 8.89 | 9.42 | 8.91 | 8.8
CZ07 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 980.6 | 2.62 | 8.93 | 9.47 | 8.95 | 8.86
CZ07 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7335.3 | 2.58 | 8.82 | 9.34 | 8.83 | 8.69
CZ07 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 867.8 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ07 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 6985 | 2.58 | 8.82 | 9.34 | 8.83 | 8.69
CZ07 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1146.2 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ07 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7342.8 | 2.58 | 8.82 | 9.34 | 8.83 | 8.69
CZ07 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 978.5 | 2.62 | 8.93 | 9.47 | 8.95 | 8.86
CZ07 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7137.7 | 2.58 | 8.81 | 9.33 | 8.83 | 8.69
CZ07 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 867 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ07 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3386.8 | 2.59 | 8.85 | 9.38 | 8.87 | 8.74
CZ07 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1154.8 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ07 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 4906.4 | 2.57 | 8.76 | 9.28 | 8.78 | 8.61
CZ07 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1151.5 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ07 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 4968.5 | 2.57 | 8.76 | 9.28 | 8.78 | 8.61
CZ07 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 865.9 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ07 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3397.6 | 2.59 | 8.85 | 9.38 | 8.87 | 8.74
CZ07 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 975.4 | 2.62 | 8.93 | 9.47 | 8.95 | 8.86
CZ07 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7173.9 | 2.58 | 8.81 | 9.33 | 8.83 | 8.68
CZ08 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1459.9 | 2.65 | 9.03 | 9.57 | 9.06 | 9.01
CZ08 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5082.3 | 2.63 | 8.96 | 9.49 | 8.98 | 8.9
CZ08 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1181.4 | 2.61 | 8.92 | 9.45 | 8.93 | 8.83
CZ08 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4301.3 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ08 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1566.3 | 2.64 | 9 | 9.53 | 9.02 | 8.95
CZ08 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5148.6 | 2.63 | 8.96 | 9.5 | 8.98 | 8.9
CZ08 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1452.3 | 2.65 | 9.03 | 9.57 | 9.05 | 9
CZ08 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 8982.9 | 2.6 | 8.87 | 9.4 | 8.89 | 8.77
CZ08 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1176.3 | 2.61 | 8.91 | 9.44 | 8.93 | 8.83
CZ08 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 8385.7 | 2.6 | 8.86 | 9.39 | 8.88 | 8.76
CZ08 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1559.5 | 2.64 | 9 | 9.53 | 9.02 | 8.95
CZ08 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 8993.3 | 2.6 | 8.86 | 9.39 | 8.88 | 8.76
CZ08 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1450.8 | 2.65 | 9.03 | 9.57 | 9.05 | 9
CZ08 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 8773.5 | 2.6 | 8.88 | 9.4 | 8.89 | 8.78
CZ08 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1174.6 | 2.61 | 8.91 | 9.44 | 8.93 | 8.83
CZ08 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4213.8 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ08 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1565.9 | 2.64 | 9 | 9.53 | 9.02 | 8.95
CZ08 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5559.8 | 2.58 | 8.79 | 9.31 | 8.81 | 8.66
CZ08 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1565.3 | 2.64 | 9 | 9.53 | 9.02 | 8.95
CZ08 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5611 | 2.58 | 8.79 | 9.31 | 8.81 | 8.66
CZ08 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1174.5 | 2.61 | 8.91 | 9.44 | 8.93 | 8.83
CZ08 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4216.2 | 2.6 | 8.88 | 9.41 | 8.9 | 8.79
CZ08 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1449.8 | 2.65 | 9.03 | 9.57 | 9.05 | 9
CZ08 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 8794.7 | 2.6 | 8.86 | 9.39 | 8.88 | 8.76
CZ09 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1560.9 | 2.63 | 8.99 | 9.52 | 9.01 | 8.94
CZ09 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5836.3 | 2.62 | 8.95 | 9.49 | 8.97 | 8.89
CZ09 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1192.6 | 2.61 | 8.91 | 9.43 | 8.92 | 8.82
CZ09 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4945 | 2.61 | 8.92 | 9.44 | 8.93 | 8.83
CZ09 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1636.6 | 2.63 | 8.97 | 9.51 | 8.99 | 8.92
CZ09 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5887.1 | 2.62 | 8.95 | 9.48 | 8.97 | 8.89
CZ09 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1556.4 | 2.63 | 8.99 | 9.52 | 9.01 | 8.94
CZ09 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9938.8 | 2.61 | 8.9 | 9.43 | 8.92 | 8.81
CZ09 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1186.7 | 2.61 | 8.91 | 9.43 | 8.92 | 8.82
CZ09 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9260.7 | 2.61 | 8.9 | 9.42 | 8.91 | 8.81
CZ09 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1631.5 | 2.63 | 8.97 | 9.51 | 8.99 | 8.92
CZ09 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9941.4 | 2.61 | 8.9 | 9.42 | 8.92 | 8.81
CZ09 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1554.4 | 2.63 | 8.99 | 9.52 | 9.01 | 8.94
CZ09 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9820.3 | 2.61 | 8.9 | 9.43 | 8.92 | 8.81
CZ09 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1185.7 | 2.61 | 8.91 | 9.43 | 8.92 | 8.82
CZ09 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4861.1 | 2.61 | 8.91 | 9.44 | 8.93 | 8.82
CZ09 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1635.1 | 2.63 | 8.97 | 9.51 | 8.99 | 8.92
CZ09 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6584.9 | 2.59 | 8.82 | 9.35 | 8.84 | 8.7
CZ09 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1635.2 | 2.63 | 8.97 | 9.51 | 8.99 | 8.92
CZ09 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6647.7 | 2.59 | 8.82 | 9.35 | 8.84 | 8.7
CZ09 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1185.8 | 2.61 | 8.91 | 9.43 | 8.92 | 8.82
CZ09 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4862.6 | 2.61 | 8.91 | 9.44 | 8.93 | 8.82
CZ09 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1554.4 | 2.63 | 8.99 | 9.52 | 9.01 | 8.94
CZ09 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9834 | 2.61 | 8.9 | 9.42 | 8.92 | 8.81
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2236.1 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6101 | 2.68 | 9.14 | 9.68 | 9.16 | 9.16
CZ10 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1576.3 | 2.7 | 9.21 | 9.76 | 9.23 | 9.26
CZ10 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4770.4 | 2.68 | 9.14 | 9.69 | 9.17 | 9.17
CZ10 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2272.7 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6110.9 | 2.68 | 9.14 | 9.68 | 9.16 | 9.16
CZ10 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2226.6 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 9368.2 | 2.64 | 9.02 | 9.56 | 9.04 | 8.99
CZ10 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1566.5 | 2.7 | 9.21 | 9.76 | 9.23 | 9.26
CZ10 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 8573.3 | 2.64 | 9.02 | 9.56 | 9.04 | 8.98
CZ10 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2263.4 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 9394.9 | 2.64 | 9.02 | 9.56 | 9.04 | 8.99
CZ10 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2224.8 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 9254.6 | 2.65 | 9.05 | 9.59 | 9.07 | 9.02
CZ10 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1564.8 | 2.7 | 9.21 | 9.76 | 9.23 | 9.26
CZ10 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 4542.5 | 2.68 | 9.15 | 9.69 | 9.17 | 9.17
CZ10 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2267.7 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6041.9 | 2.68 | 9.14 | 9.68 | 9.16 | 9.16
CZ10 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2267.9 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6048.6 | 2.68 | 9.14 | 9.68 | 9.16 | 9.16
CZ10 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1565.1 | 2.7 | 9.21 | 9.76 | 9.23 | 9.26
CZ10 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 4455.8 | 2.66 | 9.07 | 9.61 | 9.09 | 9.06
CZ10 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2225 | 2.69 | 9.18 | 9.73 | 9.2 | 9.22
CZ10 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 9286.6 | 2.65 | 9.05 | 9.59 | 9.07 | 9.02
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2645.4 | 2.67 | 9.11 | 9.65 | 9.13 | 9.12
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 7319.6 | 2.66 | 9.08 | 9.62 | 9.1 | 9.08
CZ11 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1904.6 | 2.64 | 9.02 | 9.55 | 9.04 | 8.98
CZ11 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5926.1 | 2.64 | 8.99 | 9.53 | 9.01 | 8.95
CZ11 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2695.2 | 2.65 | 9.04 | 9.58 | 9.06 | 9.02
CZ11 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 7364.9 | 2.65 | 9.04 | 9.58 | 9.06 | 9.02
CZ11 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2635.4 | 2.67 | 9.11 | 9.65 | 9.13 | 9.12
CZ11 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10879.1 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ11 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1888.8 | 2.63 | 8.98 | 9.52 | 9 | 8.93
CZ11 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9755.5 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ11 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2686.9 | 2.65 | 9.04 | 9.58 | 9.06 | 9.02
CZ11 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10897.7 | 2.62 | 8.95 | 9.48 | 8.97 | 8.88
CZ11 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2637.7 | 2.67 | 9.11 | 9.65 | 9.13 | 9.12
CZ11 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10630.9 | 2.62 | 8.95 | 9.48 | 8.97 | 8.89
CZ11 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1897.4 | 2.64 | 9.02 | 9.55 | 9.04 | 8.98
CZ11 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5839.1 | 2.63 | 8.98 | 9.51 | 9 | 8.92
CZ11 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2693.6 | 2.65 | 9.04 | 9.58 | 9.06 | 9.02
CZ11 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6767.5 | 2.58 | 8.82 | 9.34 | 8.84 | 8.69
CZ11 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2691.1 | 2.65 | 9.04 | 9.58 | 9.06 | 9.02
CZ11 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6941.3 | 2.58 | 8.82 | 9.34 | 8.83 | 8.69
CZ11 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1894.9 | 2.64 | 9.02 | 9.55 | 9.04 | 8.98
CZ11 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5837.3 | 2.63 | 8.98 | 9.51 | 9 | 8.92
CZ11 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2635.3 | 2.67 | 9.11 | 9.65 | 9.13 | 9.12
CZ11 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10674.3 | 2.62 | 8.95 | 9.49 | 8.97 | 8.89
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 1402.8 | 2.72 | 9.28 | 9.83 | 9.3 | 9.37
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 5228.6 | 2.7 | 9.21 | 9.76 | 9.23 | 9.26
CZ12 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1066.3 | 2.72 | 9.29 | 9.85 | 9.31 | 9.39
CZ12 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 4062.3 | 2.7 | 9.2 | 9.75 | 9.23 | 9.26
CZ12 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 1578.4 | 2.72 | 9.27 | 9.83 | 9.3 | 9.36
CZ12 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 5245.7 | 2.7 | 9.2 | 9.75 | 9.23 | 9.26
CZ12 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 1385.2 | 2.72 | 9.28 | 9.83 | 9.3 | 9.37
CZ12 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 7910.3 | 2.67 | 9.1 | 9.65 | 9.12 | 9.11
CZ12 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1051.5 | 2.72 | 9.29 | 9.85 | 9.32 | 9.39
CZ12 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 7260.2 | 2.67 | 9.1 | 9.64 | 9.12 | 9.1
CZ12 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 1575.1 | 2.72 | 9.27 | 9.83 | 9.3 | 9.36
CZ12 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 7934.3 | 2.66 | 9.09 | 9.63 | 9.11 | 9.09
CZ12 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 1383.5 | 2.72 | 9.28 | 9.83 | 9.3 | 9.37
CZ12 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 7768.8 | 2.67 | 9.11 | 9.66 | 9.13 | 9.12
CZ12 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1047.6 | 2.72 | 9.29 | 9.85 | 9.32 | 9.39
CZ12 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 3841.4 | 2.69 | 9.19 | 9.74 | 9.21 | 9.24
CZ12 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 1571.3 | 2.72 | 9.27 | 9.83 | 9.3 | 9.36
CZ12 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 5187.1 | 2.7 | 9.2 | 9.75 | 9.22 | 9.25
CZ12 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 1572.4 | 2.72 | 9.27 | 9.83 | 9.3 | 9.36
CZ12 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 5204.1 | 2.7 | 9.2 | 9.75 | 9.22 | 9.25
CZ12 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1050.7 | 2.72 | 9.29 | 9.85 | 9.32 | 9.39
CZ12 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 3865 | 2.69 | 9.19 | 9.74 | 9.22 | 9.24
CZ12 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 1386.4 | 2.72 | 9.27 | 9.83 | 9.3 | 9.37
CZ12 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 7865.6 | 2.67 | 9.11 | 9.65 | 9.13 | 9.11
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 3702.1 | 2.65 | 9.04 | 9.57 | 9.06 | 9.01
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 8590.3 | 2.64 | 9 | 9.54 | 9.02 | 8.96
CZ13 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2857.6 | 2.65 | 9.05 | 9.59 | 9.07 | 9.03
CZ13 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 7109.8 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ13 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3730.9 | 2.65 | 9.03 | 9.57 | 9.06 | 9.01
CZ13 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 8603 | 2.64 | 9 | 9.53 | 9.02 | 8.96
CZ13 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 3699.6 | 2.65 | 9.04 | 9.57 | 9.06 | 9.01
CZ13 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 11817 | 2.63 | 8.97 | 9.51 | 8.99 | 8.92
CZ13 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2853.8 | 2.65 | 9.05 | 9.59 | 9.07 | 9.03
CZ13 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 10437.3 | 2.62 | 8.95 | 9.48 | 8.97 | 8.89
CZ13 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3729.8 | 2.65 | 9.03 | 9.57 | 9.06 | 9.01
CZ13 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 11686.4 | 2.62 | 8.95 | 9.48 | 8.97 | 8.89
CZ13 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 3698.9 | 2.65 | 9.04 | 9.57 | 9.06 | 9.01
CZ13 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 11893.8 | 2.63 | 8.96 | 9.49 | 8.98 | 8.9
CZ13 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2849 | 2.65 | 9.05 | 9.59 | 9.07 | 9.03
CZ13 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 7020.9 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ13 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3724.5 | 2.65 | 9.03 | 9.57 | 9.06 | 9.01
CZ13 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 8568.1 | 2.64 | 9 | 9.54 | 9.02 | 8.96
CZ13 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3730 | 2.65 | 9.03 | 9.57 | 9.06 | 9.01
CZ13 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 8582.1 | 2.64 | 9 | 9.53 | 9.02 | 8.96
CZ13 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2853.5 | 2.65 | 9.05 | 9.59 | 9.07 | 9.03
CZ13 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 7031.1 | 2.64 | 9.01 | 9.54 | 9.03 | 8.97
CZ13 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3703.2 | 2.65 | 9.04 | 9.57 | 9.06 | 9.01
CZ13 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 12000.4 | 2.63 | 8.96 | 9.49 | 8.98 | 8.9
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2997.9 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 7081.2 | 2.71 | 9.25 | 9.8 | 9.27 | 9.33
CZ14 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1953.8 | 2.71 | 9.25 | 9.81 | 9.28 | 9.34
CZ14 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5287.4 | 2.71 | 9.24 | 9.8 | 9.27 | 9.32
CZ14 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3053.9 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 7110.4 | 2.71 | 9.25 | 9.8 | 9.27 | 9.32
CZ14 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2997.7 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10255 | 2.69 | 9.17 | 9.72 | 9.2 | 9.21
CZ14 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1954.7 | 2.71 | 9.25 | 9.81 | 9.28 | 9.34
CZ14 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9091.5 | 2.69 | 9.17 | 9.72 | 9.19 | 9.21
CZ14 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3054.3 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10322.6 | 2.69 | 9.17 | 9.72 | 9.19 | 9.2
CZ14 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2996.8 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10264.1 | 2.69 | 9.19 | 9.74 | 9.21 | 9.23
CZ14 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1947.1 | 2.71 | 9.25 | 9.81 | 9.28 | 9.34
CZ14 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5193.3 | 2.71 | 9.24 | 9.79 | 9.26 | 9.31
CZ14 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3046.6 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6579.4 | 2.66 | 9.07 | 9.61 | 9.09 | 9.06
CZ14 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3053.3 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6702.4 | 2.66 | 9.06 | 9.6 | 9.08 | 9.05
CZ14 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1954.2 | 2.71 | 9.25 | 9.81 | 9.28 | 9.34
CZ14 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5209 | 2.71 | 9.24 | 9.79 | 9.26 | 9.31
CZ14 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3003.5 | 2.71 | 9.25 | 9.81 | 9.28 | 9.33
CZ14 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10388.4 | 2.69 | 9.18 | 9.73 | 9.21 | 9.23
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 3840 | 2.7 | 9.23 | 9.78 | 9.25 | 9.3
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 9174.7 | 2.7 | 9.2 | 9.76 | 9.23 | 9.26
CZ15 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 2698.7 | 2.66 | 9.09 | 9.63 | 9.11 | 9.09
CZ15 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 7377.6 | 2.68 | 9.15 | 9.7 | 9.17 | 9.18
CZ15 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 3920.9 | 2.69 | 9.18 | 9.73 | 9.21 | 9.23
CZ15 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 9239.7 | 2.69 | 9.19 | 9.74 | 9.21 | 9.24
CZ15 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 3835.7 | 2.7 | 9.23 | 9.78 | 9.25 | 9.3
CZ15 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 13264.6 | 2.66 | 9.08 | 9.62 | 9.1 | 9.08
CZ15 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 2694.9 | 2.66 | 9.09 | 9.63 | 9.11 | 9.09
CZ15 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 11788.2 | 2.66 | 9.08 | 9.62 | 9.1 | 9.07
CZ15 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 3916.3 | 2.69 | 9.18 | 9.73 | 9.21 | 9.23
CZ15 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 13379 | 2.66 | 9.07 | 9.61 | 9.09 | 9.06
CZ15 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 3833.5 | 2.7 | 9.23 | 9.78 | 9.25 | 9.3
CZ15 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 13029.2 | 2.66 | 9.09 | 9.63 | 9.11 | 9.09
CZ15 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 2694.6 | 2.66 | 9.09 | 9.63 | 9.11 | 9.09
CZ15 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 7314.4 | 2.68 | 9.14 | 9.68 | 9.16 | 9.16
CZ15 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 3920.5 | 2.69 | 9.18 | 9.73 | 9.21 | 9.23
CZ15 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 8720.3 | 2.63 | 8.97 | 9.51 | 8.99 | 8.92
CZ15 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 3920.9 | 2.69 | 9.18 | 9.73 | 9.21 | 9.23
CZ15 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 8892.7 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ15 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 2695 | 2.66 | 9.09 | 9.63 | 9.11 | 9.09
CZ15 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 7313.3 | 2.65 | 9.06 | 9.6 | 9.08 | 9.04
CZ15 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 3833.8 | 2.7 | 9.23 | 9.78 | 9.25 | 9.3
CZ15 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 13180.6 | 2.66 | 9.07 | 9.61 | 9.09 | 9.05
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSE1 COOLING COIL | 2158.5 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSE27 COOLING COIL | 6787.7 | 2.6 | 8.89 | 9.41 | 8.9 | 8.79
CZ16 | 3 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E3 COOLING COIL | 1523.9 | 2.6 | 8.87 | 9.4 | 8.89 | 8.77
CZ16 | 4 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E29 COOLING COIL | 5506.5 | 2.59 | 8.83 | 9.35 | 8.85 | 8.71
CZ16 | 5 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_E5 COOLING COIL | 2206.2 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ16 | 6 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_E31 COOLING COIL | 6841.2 | 2.6 | 8.87 | 9.4 | 8.89 | 8.77
CZ16 | 7 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_SSW7 COOLING COIL | 2140.4 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ16 | 8 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_SSW33 COOLING COIL | 10809.3 | 2.56 | 8.72 | 9.23 | 8.73 | 8.55
CZ16 | 9 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W9 COOLING COIL | 1504.6 | 2.6 | 8.87 | 9.39 | 8.88 | 8.76
CZ16 | 10 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W35 COOLING COIL | 9912.4 | 2.56 | 8.72 | 9.23 | 8.73 | 8.55
CZ16 | 11 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 G_W11 COOLING COIL | 2187.6 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ16 | 12 | Coil:Cooling:DX:SingleSpeed | DXFG EL1 T_W37 COOLING COIL | 10906.6 | 2.56 | 8.72 | 9.23 | 8.73 | 8.55
CZ16 | 13 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WSW1 COOLING COIL | 2139 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ16 | 14 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WSW27 COOLING COIL | 10557 | 2.56 | 8.73 | 9.24 | 8.74 | 8.56
CZ16 | 15 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S3 COOLING COIL | 1503 | 2.6 | 8.87 | 9.39 | 8.88 | 8.76
CZ16 | 16 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S29 COOLING COIL | 5287 | 2.58 | 8.8 | 9.32 | 8.81 | 8.66
CZ16 | 17 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_S5 COOLING COIL | 2200.2 | 2.61 | 8.92 | 9.45 | 8.94 | 8.84
CZ16 | 18 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_S31 COOLING COIL | 6742.7 | 2.59 | 8.85 | 9.38 | 8.87 | 8.74
CZ16 | 19 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N11 COOLING COIL | 2200.4 | 2.62 | 8.92 | 9.45 | 8.94 | 8.84
CZ16 | 20 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N37 COOLING COIL | 6722.9 | 2.59 | 8.82 | 9.34 | 8.84 | 8.7
CZ16 | 21 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_N9 COOLING COIL | 1501.3 | 2.6 | 8.87 | 9.39 | 8.88 | 8.76
CZ16 | 22 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_N35 COOLING COIL | 5284.6 | 2.57 | 8.77 | 9.29 | 8.78 | 8.62
CZ16 | 23 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 G_WNW7 COOLING COIL | 2137.5 | 2.62 | 8.94 | 9.47 | 8.96 | 8.87
CZ16 | 24 | Coil:Cooling:DX:SingleSpeed | DXFG EL2 T_WNW33 COOLING COIL | 10676.3 | 2.56 | 8.72 | 9.23 | 8.73 | 8.55
SWHC031-03 Furnace_SFm_1985 | SFm&1&rNCGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ10 | 1 | DXGF EL7 | Cooling | Sensible | 2750.25 | 0.15331 | 0.15331 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL7 | Heating | Sensible | 3308.71 | 0.0939 | 0.0939 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL8 | Cooling | Sensible | 3158.56 | 0.17641 | 0.17641 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL8 | Heating | Sensible | 3307.65 | 0.0938 | 0.0938 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL7 | Cooling | Sensible | 3623.66 | 0.21231 | 0.21231 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL7 | Heating | Sensible | 4997.83 | 0.13879 | 0.13879 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL8 | Cooling | Sensible | 4239.99 | 0.2489 | 0.2489 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL8 | Heating | Sensible | 4996.37 | 0.13875 | 0.13875 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL7 | Cooling | Sensible | 2808.12 | 0.16207 | 0.16207 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL7 | Heating | Sensible | 4574.79 | 0.12612 | 0.12612 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL8 | Cooling | Sensible | 3399.36 | 0.19654 | 0.19654 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL8 | Heating | Sensible | 4568.38 | 0.12594 | 0.12594 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL7 | Cooling | Sensible | 3872.04 | 0.22277 | 0.22277 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL7 | Heating | Sensible | 4369.72 | 0.12177 | 0.12177 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL8 | Cooling | Sensible | 4555.7 | 0.26613 | 0.26613 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL8 | Heating | Sensible | 4368.47 | 0.12174 | 0.12174 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL7 | Cooling | Sensible | 3733.5 | 0.20972 | 0.20972 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL7 | Heating | Sensible | 2487.89 | 0.0802 | 0.0802 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL8 | Cooling | Sensible | 4246.74 | 0.23855 | 0.23855 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL8 | Heating | Sensible | 2486.17 | 0.0801 | 0.0801 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL7 | Cooling | Sensible | 4943.05 | 0.28061 | 0.28061 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL7 | Heating | Sensible | 3487.47 | 0.0995 | 0.0995 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL8 | Cooling | Sensible | 5582.92 | 0.32044 | 0.32044 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL8 | Heating | Sensible | 3483.87 | 0.0994 | 0.0994 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL7 | Cooling | Sensible | 2325.75 | 0.15727 | 0.15727 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL7 | Heating | Sensible | 4159.68 | 0.11252 | 0.11252 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXGF EL8 | Cooling | Sensible | 2983.35 | 0.20069 | 0.20069 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL8 | Heating | Sensible | 4160.68 | 0.11255 | 0.11255 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
SWHC031-03 Furnace_SFm_1985 | SFm&1&rDXGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ10 | 1 | DXGF EL7 | Cooling | Sensible | 2750.25 | 0.15331 | 0.15331 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL7 | Heating | Sensible | 3308.71 | 0.0939 | 0.0939 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL8 | Cooling | Sensible | 3158.56 | 0.17641 | 0.17641 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL8 | Heating | Sensible | 3307.65 | 0.0938 | 0.0938 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL7 | Cooling | Sensible | 3623.66 | 0.21231 | 0.21231 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL7 | Heating | Sensible | 4997.83 | 0.13879 | 0.13879 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL8 | Cooling | Sensible | 4239.99 | 0.2489 | 0.2489 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL8 | Heating | Sensible | 4996.37 | 0.13875 | 0.13875 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL7 | Cooling | Sensible | 2808.12 | 0.16207 | 0.16207 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL7 | Heating | Sensible | 4574.79 | 0.12612 | 0.12612 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL8 | Cooling | Sensible | 3399.36 | 0.19654 | 0.19654 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL8 | Heating | Sensible | 4568.38 | 0.12594 | 0.12594 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL7 | Cooling | Sensible | 3872.04 | 0.22277 | 0.22277 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL7 | Heating | Sensible | 4369.72 | 0.12177 | 0.12177 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL8 | Cooling | Sensible | 4555.7 | 0.26613 | 0.26613 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL8 | Heating | Sensible | 4368.47 | 0.12174 | 0.12174 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL7 | Cooling | Sensible | 3733.5 | 0.20972 | 0.20972 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL7 | Heating | Sensible | 2487.89 | 0.0802 | 0.0802 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL8 | Cooling | Sensible | 4246.74 | 0.23855 | 0.23855 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL8 | Heating | Sensible | 2486.17 | 0.0801 | 0.0801 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL7 | Cooling | Sensible | 4943.05 | 0.28061 | 0.28061 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL7 | Heating | Sensible | 3487.47 | 0.0995 | 0.0995 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL8 | Cooling | Sensible | 5582.92 | 0.32044 | 0.32044 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL8 | Heating | Sensible | 3483.87 | 0.0994 | 0.0994 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL7 | Cooling | Sensible | 2325.75 | 0.15727 | 0.15727 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL7 | Heating | Sensible | 4159.68 | 0.11252 | 0.11252 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
CZ16 | 3 | DXGF EL8 | Cooling | Sensible | 2983.35 | 0.20069 | 0.20069 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL8 | Heating | Sensible | 4160.68 | 0.11255 | 0.11255 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 45313
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3235 | 2.83 | 9.67 | 10.27 | 9.71 | 9.99
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3668.6 | 2.83 | 9.65 | 10.24 | 9.69 | 9.96
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4160.8 | 2.81 | 9.57 | 10.16 | 9.61 | 9.83
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 4864.9 | 2.8 | 9.57 | 10.15 | 9.6 | 9.83
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 3242.1 | 2.81 | 9.6 | 10.19 | 9.64 | 9.88
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3900.5 | 2.81 | 9.59 | 10.18 | 9.63 | 9.86
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4562.8 | 2.82 | 9.63 | 10.22 | 9.67 | 9.93
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5335 | 2.81 | 9.6 | 10.19 | 9.64 | 9.88
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 4490 | 2.84 | 9.69 | 10.29 | 9.73 | 10.02
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 5050 | 2.84 | 9.68 | 10.27 | 9.71 | 10
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 5946.1 | 2.84 | 9.68 | 10.27 | 9.72 | 10
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 6704.8 | 2.83 | 9.66 | 10.25 | 9.7 | 9.97
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL7 COOLING COIL | 2785.8 | 2.76 | 9.43 | 10 | 9.46 | 9.6
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL8 COOLING COIL | 3568.6 | 2.76 | 9.43 | 10.01 | 9.46 | 9.61
SWHC031-03 Furnace_SFm_1985 | SFm&2&rNCGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ10 | 1 | DXGF EL2 | Cooling | Sensible | 13855.86 | 0.76859 | 0.76859 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL2 | Heating | Sensible | 8453.96 | 0.23984 | 0.23984 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL5 | Cooling | Sensible | 11529.8 | 0.64264 | 0.64264 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL5 | Heating | Sensible | 8434.43 | 0.23928 | 0.23928 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL2 | Cooling | Sensible | 16147.55 | 0.94307 | 0.94307 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL2 | Heating | Sensible | 12430.2 | 0.34555 | 0.34555 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL5 | Cooling | Sensible | 12743.9 | 0.73374 | 0.73374 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL5 | Heating | Sensible | 12409.07 | 0.34497 | 0.34497 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL2 | Cooling | Sensible | 14261.33 | 0.81597 | 0.81597 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL2 | Heating | Sensible | 10515.94 | 0.2899 | 0.2899 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL5 | Cooling | Sensible | 10846.86 | 0.60928 | 0.60928 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL5 | Heating | Sensible | 10484.75 | 0.28904 | 0.28904 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL2 | Cooling | Sensible | 17487.7 | 1.006 | 1.006 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL2 | Heating | Sensible | 10665.66 | 0.29722 | 0.29722 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL5 | Cooling | Sensible | 13171.17 | 0.76595 | 0.76595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL5 | Heating | Sensible | 10640.14 | 0.2965 | 0.2965 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL2 | Cooling | Sensible | 16355.95 | 0.91876 | 0.91876 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL2 | Heating | Sensible | 9823.84 | 0.31661 | 0.31661 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL5 | Cooling | Sensible | 12213.31 | 0.68606 | 0.68606 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL5 | Heating | Sensible | 9792.05 | 0.31559 | 0.31559 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL2 | Cooling | Sensible | 18766.46 | 1.0581 | 1.0581 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL2 | Heating | Sensible | 9606.2 | 0.27377 | 0.27377 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL5 | Cooling | Sensible | 15178.79 | 0.8956 | 0.8956 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL5 | Heating | Sensible | 9580.78 | 0.27305 | 0.27305 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL2 | Cooling | Sensible | 13775.5 | 0.92179 | 0.92179 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL2 | Heating | Sensible | 10569.77 | 0.2859 | 0.2859 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL5 | Cooling | Sensible | 9976.87 | 0.6982 | 0.6982 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL5 | Heating | Sensible | 10540.73 | 0.28512 | 0.28512 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
SWHC031-03 Furnace_SFm_1985 | SFm&2&rDXGF&Ex&SpaceHtg_eq__GasFurnace | AFUE_80_baseline
System Sizing Information
CZ |  | System Name | Load Type | Peak Load Kind | User Design Capacity | Calc Des Air Flow Rate [m3/s] | User Des Air Flow Rate [m3/s] | Design Day Name | Date/Time of Peak
CZ10 | 1 | DXGF EL2 | Cooling | Sensible | 13855.86 | 0.76859 | 0.76859 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 2 | DXGF EL2 | Heating | Sensible | 8453.96 | 0.23984 | 0.23984 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ10 | 3 | DXGF EL5 | Cooling | Sensible | 11529.8 | 0.64264 | 0.64264 | CA_RIVERSIDE-MUNI ANN CLG .4% CONDNS DB=>MWB | 2024-08-21
CZ10 | 4 | DXGF EL5 | Heating | Sensible | 8434.43 | 0.23928 | 0.23928 | CA_RIVERSIDE-MUNI ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ11 | 1 | DXGF EL2 | Cooling | Sensible | 16147.55 | 0.94307 | 0.94307 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 2 | DXGF EL2 | Heating | Sensible | 12430.2 | 0.34555 | 0.34555 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ11 | 3 | DXGF EL5 | Cooling | Sensible | 12743.9 | 0.73374 | 0.73374 | CA_RED-BLUFF-MUNI-AP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ11 | 4 | DXGF EL5 | Heating | Sensible | 12409.07 | 0.34497 | 0.34497 | CA_RED-BLUFF-MUNI-AP ANN HTG 99.6% CONDNS DB | 2024-12-21 08:00
CZ12 | 1 | DXGF EL2 | Cooling | Sensible | 14261.33 | 0.81597 | 0.81597 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 2 | DXGF EL2 | Heating | Sensible | 10515.94 | 0.2899 | 0.2899 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ12 | 3 | DXGF EL5 | Cooling | Sensible | 10846.86 | 0.60928 | 0.60928 | CA_STOCKTON-METRO-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ12 | 4 | DXGF EL5 | Heating | Sensible | 10484.75 | 0.28904 | 0.28904 | CA_STOCKTON-METRO-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 15:00
CZ13 | 1 | DXGF EL2 | Cooling | Sensible | 17487.7 | 1.006 | 1.006 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 2 | DXGF EL2 | Heating | Sensible | 10665.66 | 0.29722 | 0.29722 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ13 | 3 | DXGF EL5 | Cooling | Sensible | 13171.17 | 0.76595 | 0.76595 | CA_FRESNO-YOSEMITE-IAP ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ13 | 4 | DXGF EL5 | Heating | Sensible | 10640.14 | 0.2965 | 0.2965 | CA_FRESNO-YOSEMITE-IAP ANN HTG 99.6% CONDNS DB | 2024-12-21 15:00
CZ14 | 1 | DXGF EL2 | Cooling | Sensible | 16355.95 | 0.91876 | 0.91876 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 2 | DXGF EL2 | Heating | Sensible | 9823.84 | 0.31661 | 0.31661 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ14 | 3 | DXGF EL5 | Cooling | Sensible | 12213.31 | 0.68606 | 0.68606 | CA_DAGGETT-BARSTOW-DAGGE ANN CLG .4% CONDNS DB=>MWB | 2024-07-21
CZ14 | 4 | DXGF EL5 | Heating | Sensible | 9792.05 | 0.31559 | 0.31559 | CA_DAGGETT-BARSTOW-DAGGE ANN HTG 99.6% CONDNS DB | 45648
CZ15 | 1 | DXGF EL2 | Cooling | Sensible | 18766.46 | 1.0581 | 1.0581 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 2 | DXGF EL2 | Heating | Sensible | 9606.2 | 0.27377 | 0.27377 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ15 | 3 | DXGF EL5 | Cooling | Sensible | 15178.79 | 0.8956 | 0.8956 | CA_EL-CENTRO-NAF ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ15 | 4 | DXGF EL5 | Heating | Sensible | 9580.78 | 0.27305 | 0.27305 | CA_EL-CENTRO-NAF ANN HTG 99.6% CONDNS DB | 2024-01-21 08:00
CZ16 | 1 | DXGF EL2 | Cooling | Sensible | 13775.5 | 0.92179 | 0.92179 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 2 | DXGF EL2 | Heating | Sensible | 10569.77 | 0.2859 | 0.2859 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
CZ16 | 3 | DXGF EL5 | Cooling | Sensible | 9976.87 | 0.6982 | 0.6982 | CA_BISHOP-AP ANN CLG 0.4% CONDNS DB=>MCWB | 2024-07-21
CZ16 | 4 | DXGF EL5 | Heating | Sensible | 10540.73 | 0.28512 | 0.28512 | CA_BISHOP-AP ANN HTG 99.6% CONDNS DB | 2024-01-21 17:50
DX Cooling Coil Standard Rating Information
CZ |  | Component Type | Component Name | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER User {Btu/W-h} | SEER Standard {Btu/W-h} | IEER {Btu/W-h}
CZ10 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 15644.8 | 2.82 | 9.62 | 10.21 | 9.66 | 9.91
CZ10 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 13213.2 | 2.82 | 9.64 | 10.23 | 9.68 | 9.94
CZ11 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 18467.8 | 2.81 | 9.57 | 10.16 | 9.61 | 9.83
CZ11 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14680.1 | 2.81 | 9.6 | 10.19 | 9.64 | 9.88
CZ12 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 16078.3 | 2.81 | 9.58 | 10.17 | 9.62 | 9.84
CZ12 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 12350.9 | 2.82 | 9.62 | 10.21 | 9.66 | 9.91
CZ13 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 20129.2 | 2.81 | 9.6 | 10.19 | 9.64 | 9.88
CZ13 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 15266.3 | 2.81 | 9.6 | 10.18 | 9.63 | 9.87
CZ14 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 19311.6 | 2.83 | 9.67 | 10.26 | 9.71 | 9.98
CZ14 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 14686.1 | 2.84 | 9.69 | 10.29 | 9.73 | 10.02
CZ15 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 22494.7 | 2.84 | 9.68 | 10.28 | 9.72 | 10.01
CZ15 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 18142.5 | 2.82 | 9.62 | 10.21 | 9.65 | 9.9
CZ16 | 1 | Coil:Cooling:DX:SingleSpeed | DXGF EL2 COOLING COIL | 16282.9 | 2.76 | 9.42 | 10 | 9.45 | 9.6
CZ16 | 2 | Coil:Cooling:DX:SingleSpeed | DXGF EL5 COOLING COIL | 11633.3 | 2.74 | 9.34 | 9.9 | 9.36 | 9.46
We found the same numbers in our output, however, we pulled different numbers for the coil size. This is the interim sizing step where the heating and cooling loads are calculated from the design day. For this heat pump the heating and cooling loads are very different so E+ chose a system with capacity in between at approx 3000 W.
https://bigladdersoftware.com/epx/docs/24-1/engineering-reference/component-sizing.html#dx-coil-sizing:~:text=For%20Coil%3AHeating%3ADX%3ASingleSpeed%20the%20rated%20heating%20capacity%20is%20set%20equal%20to%20the%20cooling%20capacity.

## Legend
Outputs from E+ on Results Summary tabs
included | AnnualBuildingUtilityPerformanceSummary/Entire Facility/Building Area/Area/Net Conditioned Building Area, Conditioned Area
included | ComponentSizingSummary/Entire Facility/Coil:Cooling:DX:SingleSpeed/Design Size Gross Rated Total Cooling Capacity/*, DX Coil Cool Capacity
excluded | ComponentSizingSummary/Entire Facility/Coil:Cooling:DX:MultiSpeed/Design Size Speed 1 Gross Rated Total Cooling Capacity/*, MZ Coil Cool Capacity
excluded | ComponentSizingSummary/Entire Facility/Coil:Cooling:Water/Design Size Design Coil Load/*, Water Coil Cool Capacity
excluded | ComponentSizingSummary/Entire Facility/Coil:Heating:DX:SingleSpeed/Design Size Gross Rated Total Heating Capacity/*, DX Coil Heat Capacity | The heat pump heating capacity is the same as the heat pump cooling capacity.
excluded | ComponentSizingSummary/Entire Facility/Coil:Heating:DX:MultiSpeed/Design Size Speed 1 Gross Rated Total Heating Capacity/*, MZ Coil Heat Capacity
included | ComponentSizingSummary/Entire Facility/Coil:Heating:Fuel/Design Size Nominal Capacity/*, Fuel Coil Heat Capacity
included | ComponentSizingSummary/Entire Facility/Coil:Heating:Electric/Design Size Nominal Capacity/*, Elec Coil Heat Capacity